## INDEX
Links to this File's Tables and Notes
Table YE1 | Definitions for the Different Interface Points
Table YE2 | Yield Enhancement Difficult Challenges
Table YE3 | Technology Requirements for Surface Environmental Contamination Control
Table YE3a | Limit values for interfering atoms on surfaces; avoidance of critical defect densities, various process stages (from the chapter More Moore)
Table YE3b | Model results critical times (tcrit) to reach the limit values for impurity atoms for different process stages; model substances
Table YE4 | AMC Monitoring Methods
Table YE4a | Supporting Table for On-line Methods
Table YE5 | Yield requirements for MEMS production
Table YE6 | Bulk Gases Supporting Table for On-line Methods
Table Notes
Table YE3 notes
Table YE4 notes
Table YE4a notes
Table YE5 notes
© 2023 IEEE. Personal use of this material is permitted. Permission from IEEE must be obtained for all other uses, in any current or future media, including reprinting/republishing this material for advertising or promotional purposes, creating new collective works, for resale or redistribution to servers or lists, or reuse of any copyrighted component of this work in other works.

## Table YE1
INDEX
Table YE1 Definitions for the Different Interface Points
|  | POS | POD | POC | POE | POU | POP
|  |  | Point of Delivery |  | Point of Entry | Point of Use | Point of Process
|  | Delivery Point of Gas/Chemical Supplier | Outlet of Central Facility System | Submain or VMB/VMP Take off Valve | Entry to Equipment or Sub Equipment | Entry to the Process Chamber | Contact with Wafer
| Ultrapure water | Raw water | Outlet of final filtration in UPW plant | Outlet of submain take off valve | Inlet of wet bench or subequipment | Inlet of wet bench bath, spray nozzle, or connection point to piping, which is also used for other chemicals | Wafer in production
| Process chemicals | Chemical drum/tote/bulk supply | Outlet of final filtration of chemical distribution unit | Outlet of VMB valve | Inlet of wet bench or intermediate tank | Inlet of wet bench bath or spray nozzle | Wafer in production
| Specialty gases | Gas cylinder or bulk specialty gas systems | Outlet of final filtration of gas cabinet | Outlet of VMB valve | Inlet of equipment | Inlet of chamber (outlet of MFC) | Wafer in production
| Bulk gases | Bulk gas delivered on site or gas generator | Outlet of final filtration/purification | Outlet of submain take off valve or VMB valve | Inlet of equipment/ subequipment | Inlet of chamber (outlet of MFC) | Wafer in production
| Cleanroom and AMC | Outside air | Outlet of make-up air handling unit | Outlet of filters in cleanroom ceiling | Inside of mini-environment or sub equipment for AMC and particles, behind MNEV filters | Gas/air in vicinity to wafer/substrate | Wafer/substrate in production (AMC/ SMC)

## Table YE2
INDEX | Table YE2 Yield Enhancement Difficult Challenges – 2023 update SECC
IS | Near-Term Challenges: 2022-2028 | Description
| Challenge #1 Control of Electrically Active and other particles in Ultrapure Water and Liquid Chemicals for advanced semiconductor manufacturing (logic key driver) | Insufficient metrology and marginal treatment technology capability
| Challenge #2 Control of Electrically Active and other particles in UPW of EUV mask production | Insufficient metrology and marginal treatment technology capability
| Challenge #3 Critical Organics in UPW | Insufficient metrology for online speciation of organics
| Challenge #4 Metals in H2O2 | Insufficient metrology capability. Characterization needed for specific critical metals for key process steps and segments.
| Challenge #5 Slurry particle characterization and other impurity monitoring | Insufficient metrology capability
| Challenge #6 Plating chemicals: particles > critical size (>0.150 µm) (#/ml) | Need reliable monitoring of large particles
| Challenge #7 Liquid Chemicals: particles > critical size (#/ml) | Need reliable monitoring of particles <10 nm. Need Filtration technology that is reliable at the stated retention rating and that has minimal "rise up" contributions at the time of install into the process.
| Challenge #8 CMP Slurries: large particles > MPS (#/ml) | Need reliable LPC metrology that can measure targeted particles sizes and concentrations that ignore the MPS sizes and do not require sample dilution to obtain the measurement.
| Challenge #9 Post-CMP (pCMP) Cleans particles | Some pCMP cleans will have volatile or highly reactive ingredients that form bubbles in solution, therefore; new metrology and new techniques will be needed to differentiate between bubbles and real particles for contamination control. The pCMP cleans that contain surfactants will have micelle particles and structures that are necessary for the chemistry to perform the intended function. The need is for reliable and accurate metrology to distinguish micelles from other foreign particles in solution.
| Challenge #10 Particle measurement for ISO class 1 | Need more efficient and effective laser particle counters with detection limit << 100 nm or CPC with sample flow >> 0,1 cfm
| Challenge #11 AMC metrology | Need of more sensitive gas analyzers for HCl, HF, HNO3, HBr, NH3, Total Acids, H2S, SO2, organic acids, sulphuric acids and Total bases with detection limit << 100 ppt
| Challenge #12 Particle contribution by critical components and its control | Insufficient analytical capability and unknown level of cleanliness
New | Challenge #13 Critical metals in UPW for CMOS image sensors | Insufficient metrology sensitivity below 200 ppq concentration
New | Challenge #14 Low concentration particle measurement in the 10-100nm range to check the cleanliness of gases and to judge the contribution to particle cleanliness from hardware present in the gas delivery system (upstream or downstream from POD). | Preferably these measurements should be possible at a freely selectable flowrate instead of fixed 1 cfm or 0.1 cfm
New | Challenge #15 Composition and/or structural information for <100nm particles, especially when present in small numbers. | Low amounts of particles have the potential of creating issues. Having excess to techniques that can learn about elemental composition and/or chemical structures can help a lot in root cause finding of observed issues.
New | Challenge #16 Particulate precursor metrology < 10 nm | Need better understanding of particle precursors and critical concentrations to form particles. Important to determine relationship between species/concentrations and particle size.
New | Challenge #17 Removing particles < 30 nm | Overcoming the static/van der Waals forces that make particles adhere to critical surfaces is much more difficult for particles < 30 nm.
IS | Long-Term Challenges: 2029–2037 | Description
OUT OF CURRENT SCOPE OF YIELD ENHANCEMENT

## Table YE3
INDEX |  | Table YE3 Technology Requirements for Surface Environmental Contamination Control
|  | Year of Production | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | Remarks | Driver, actions required
Add Pitch designation
Add Pitch designation
|  | Logic industry "Node Range" Labeling (nm) | "5" | "3" | "3" | "3" | "2.1" | "2.1" | "2.1"
|  | IDM-Foundry node labeling | i7-f5 | i3-f2.1 | i3-f2.1 | i3-f2.1 | i2.1-f1.5 | i2.1-f1.5 | i2.1-f1.5
|  | Logic device structure options | FinFET | finFET LGAA | finFET LGAA | finFET LGAA | LGAA | LGAA | LGAA
|  | Logic device mainstream device | FinFET | finFET | finFET | finFET | LGAA | LGAA | LGAA
|  | MPU/SoC Metalx ½ Pitch (nm)[1,2] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | based on More Moore table
|  | Critical particle size non-electrically active (non-EAP) (nm) based on 50% of Logic 1/2 Pitch (nm (contacted) [1] | 10 | 9 | 9 | 9 | 7 | 7 | 7 | based on input from MM
|  | Critical particle size (nm) of Electrically Active particles based on 50% width of fin Logic SiGe Front End or other device critical dimensions for LGAA (>2 monolayers) | 3.5 | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | based on input from MM
|  | Critical size (EUV mask), nm | 12 | 12 | 12 | 12 | 12 | 12 | 12 | function of the wavelength
Wafer Environment Particle Contaminants in Gas Phase (reg. ISO 14644-1)
|  | Number of particles (/m3) [1] [2] | ISO CL1 | ISO CL1 | ISO CL1 | ISO CL1 | ISO CL1 | ISO CL1 | ISO CL1
Airborne Molecular Contaminants in Gas Phase (pptV, V for Volume)) [3, 7, 12,13,15,33].
Gate stack (Gate oxide and gate oxide pre-clean), POE (Point of Entry)
|  | Total Inorganic Acids (HF, HCl, HBr, HNO3, H3PO4, H2SO4, excluded HNO2); POE | 4000 (total) / 500 (individual) | 2000 (total) / 500 (individual) | 2000 (total) / 500 (individual) | 2000 (total) / 500 (individual) | tbd | tbd | tbd
|  | Total Organic and Inorganic Bases | 1000 | 1000 | 1000 | 1000 | tbd | tbd | tbd
|  | Total Organics > C6 , (aliphatics, conjugated, ketones, aldehydes, esters and others w/ GCMS retention times ≥ benzene, calibrated to hexadecane) [31] POE | 1000 | 1000 | 1000 | 1000 | tbd | tbd | tbd |  |  |  | tbd
|  | Total Organic Compounds and Inorganic compounds that contain P, B, As (Dopants), POE. | 100 | 100 | 100 | 100 | tbd | tbd | tbd
Source Drain Contact module (Trench Etch & EPI), POE (Point of Entry)
|  | Inorganic Acids (HF, HCl, HBr, HNO3, H3PO4, H2SO4, H2SO3, SO2; excluded HNO2), each; POE | 10 | 10 | 10 | 10 | tbd | tbd | tbd
|  | Total Organic and Inorganic Bases; POE | 100 | 100 | 100 | 100 | tbd | tbd | tbd
|  | Total Organic Acids [30]; POE | 100 | 100 | 100 | 100 | tbd | tbd | tbd
|  | Total Organics > C6 , (aliphatics, conjugated, ketones, aldehydes, esters and others w/ GCMS retention times ≥ benzene, calibrated to hexadecane) [31] [52] | 100 | tbd | tbd | tbd | tbd | tbd | tbd
|  | Total Organics > C6 , (aliphatics, conjugated, ketones, aldehydes, esters and others w/ GCMS retention times ≥ benzene, calibrated to hexadecane) [31]; POE | 100 | 100 | 100 | 100 | tbd | tbd | tbd
|  | Total Organic Acids [30]; POE | 500 | 500 | 500 | 500 | tbd | tbd | tbd
|  | Reactive Sulfur compounds (e.g.: H2S); POE | 500 | 500 | 500 | 500 | tbd | tbd | tbd
|  | Total Organics > C6 , (aliphatics, conjugated, ketones, aldehydes, esters and others w/ GCMS retention times ≥ benzene, calibrated to hexadecane) [31] [52] POE | 1000 | tbd | tbd | tbd | tbd | tbd | tbd
|  | Total Organics > C6 , (aliphatics, conjugated, ketones, aldehydes, esters and others w/ GCMS retention times ≥ benzene, calibrated to hexadecane) [31]; POE | 1000 | 1000 | 1000 | 1000 | tbd | tbd | tbd
|  | Oxidizers (e.g. Ozone); POE | 5000 | 5000 | 5000 | 5000 | tbd | tbd | tbd
Ultrapure Water [29]
|  | Total organic carbon (ppb) [22] for immersion litho, POE | <1 | <1 | <1 | <1 | <1 | <1 | <1 |  | lense hazing
|  | Critical Organics as C (ppb) [22], POE | <1 | <1 | <1 | <1 | <1 | <1 | <1 |  | 1E+12 at/cm2 of C on the wafer
|  | Non-critical organics as C (ppb) [22], POE | <3 | <3 | <3 | <3 | <3 | <3 | <3 |  | typical UPW system capability
|  | Reactive silica (ppb) as SiO2 [18], POC | <0.05 | <0.05 | <0.05 | <0.05 | <0.05 | <0.05 | <0.05
|  | PROACTIVE: Reactive silica (ppb) as SiO2 [18], [FEED to UPW TANK] | <0.05 | <0.05 | <0.05 | <0.05 | <0.05 | <0.05 | <0.05 |  | driven by proactive TM needs
|  | Critical particle size non-electrically active (non-EAP) (nm) based on 50% of Logic 1/2 Pitch (nm (contacted) [1] | 10 | 9 | 9 | 9 | 7 | 7 | 7 | based on input from MM
|  | Number of non-EAP at critical size (#/ml) [26], POE | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | Critical particle size (nm) of Electrically Active particles based on 50% width of fin Logic SiGe Front End or other device critical dimensions for LGAA (>2 monolayers) | 3.5 | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | based on input from MM
|  | Number of EAP at critical particle size (#/ml) [26], POP | 100 | 100 | 100 | 100 | 10 | 10 | 10 | EAP - electrically active (conductive) particles | electrical conductivity may be lower for very small particles - needs further investigation
|  | Critical size (EUV mask), nm | 12 | 12 | 12 | 12 | 12 | 12 | 12 | function of the wavelength
|  | Number of particles for EUV mask production (#/ml) [26.3], POE | 1 | 1 | 1 | 1 | 1 | 1 | 1 | An order of magnitude stricter than FAB
|  | PROACTIVE: Particle Control: 50nm (#/L) [26], Feed to the Final Filter. Values with (*) require particle control at 30nm size and arger. [refer to the Particle White Paper] | <50 | <50 | <50 | <50 | <50* | <50* | <50* | based on assumed filter retention and power law calculation
|  | Particle Precursors, #/ml [56] | 1 (see note) | 1 (see note) | 2 (see note) | 3 (see note) | 4 (see note) | 5 (see note) | 6 (see note)
|  | Particle Precursors, #/ml [56] | 20,000 (see note) | 20,000 (see note) | 20,000 (see note) | 20,000 (see note) | 20,000 (see note) | 20,000 (see note) | 20,000 (see note) | this level is expected to produce 5 particles per 300 mm wafer of 10nm particles and greater.
|  | Dissolved oxygen (ppb) (contaminant based) [16] POE | <10 | <10 | <10 | <10 | <10 | <10 | <10
|  | Dissolved nitrogen (ppm) [10] POE | 8–18 | 8–18 | 8–18 | 8–18 | 8–18 | 8–18 | 8–18
|  | Hydrogen Peroxide (ppb) [42] POD | <3 | <3 | <3 | <3 | <3 | <3 | <3 | consistent with DO and supported by experiment
|  | Metals (ppt each) (Al, As, Ba, Ca, Cd, Co, Cr, Cu, Fe, K, Li, Mg, Mn, Mo, Na, Ni, Pb, Sb, Sn, Sr, Ti, V, W, Zn + Pt*) [39], POP | <1 | <1 | <1 | <1 | <1 | <1 | <1
|  | Proactive: Critical Metals for image sensors (ppt each) (Mo, W, Ti, Au*, Pt*, Cu, Mn, Ag*, Co) [39], Feed to UPW tank | 1 | 1 | 1 | 1 | 1 | 1 | 1 | Also recommend resin QC with SEMI C93 (acid leach)
|  | Critical Metals for image sensors (ppt each) (Mo, W, Ti, Au*) [39], POP | <0.05 | <0.05 | <0.05 | <0.05 | <0.05 | <0.05 | <0.05
|  | Critical Metals for image sensors (ppt each) (Pt*, Cu, Mn, Ag*, Co) [39], POP | <0.2 | <0.2 | <0.2 | <0.2 | <0.2 | <0.2 | <0.2
|  | Other critical ions in ambient UPW (ppt each) [24], POP | <50 | <50 | <50 | <50 | <50 | <50 | <50
|  | Phosphate as HPO4 (ppt), POP | <20 | <20 | <20 | <20 | <20 | <20 | <20
|  | Boron (ppt) [24], POP | <50 | <50 | <50 | <50 | <50 | <50 | <50
|  | Temperature stability (K) [38], POE | ± 1 | ± 1 | ± 1 | ± 1 | ± 1 | ± 1 | ± 1
|  | Temperature gradient in K/10 minutes [38] for immersion litho, POE [38] | <0.1 | <0.1 | <0.1 | <0.1 | <0.1 | <0.1 | <0.1
Liquid Chemicals
|  | 49% HF metals Al, As, Ba, Ca, Cd, Co, Cr, Cu, Fe, K, Li, Mg, Mn, Mo, Na, Ni, Pb, Sb, Sn, Sr, Ti, V, W, Zn + Pt POP cleaning chemistry (ppt) | 20 | 20 | 20 | 20 | 20 | 20 | 10
|  | 49% HF metals Al, As, Ba, Ca, Cd, Co, Cr, Cu, Fe, K, Li, Mg, Mn, Mo, Na, Ni, Pb, Sb, Sn, Sr, Ti, V, W, Zn + Pt POP cleaning chemistry (ppt) | 20 | 20 | 20 | 20 | 20 | 20 | 10
|  | 49% HF cleaning Anions (ppb) | 250 | 200 | 200 | 200 | 200 | 200 | 200
|  | 49% HF cleaning Cl | 50 | 40 | 40 | 40 | 40 | 40 | 40
|  | 49% HF cleaning Assay Variance | 0.05 | 0.05 | 0.02 | 0.02 | 0.01 | 0.01 | 0.01
|  | 49% HF cleaning particle counts POP (20 nm/ml) | 45 | 40 | 35 | 30 | 25 | 20 | 15
|  | 49% HF cleaning particle counts supplier (20 nm/ml) | 450 | 400 | 350 | 300 | 250 | 200 | 150
|  | 49% HF Cleaning Elemental Free Carbon | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | 49% HF Etch metals Al, As, Ba, Ca, Cd, Co, Cr, Cu, Fe, K, Li, Mg, Mn, Mo, Na, Ni, Pb, Sb, Sn, Sr, Ti, V, W, Zn + Pt from supplier (ppt) | 20 | 20 | 20 | 20 | 20 | 10 | 10
|  | 49% HF metals Al, As, Ba, Ca, Cd, Co, Cr, Cu, Fe, K, Li, Mg, Mn, Mo, Na, Ni, Pb, Sb, Sn, Sr, Ti, V, W, Zn + Pt POP etch (ppt) | 20 | 20 | 20 | 20 | 20 | 10 | 10
|  | 49% HF etch Anions (ppb) | 250 | 200 | 200 | 200 | 200 | 200 | 200
|  | 49% HF etch Cl (ppb) | 50 | 40 | 40 | 40 | 40 | 40 | 40
|  | 49% HF etch Assay Variance (%) | 0.05 | 0.05 | 0.02 | 0.02 | 0.01 | 0.01 | 0.01
|  | 49% HF Etch Particle Counts Supplier (20 nm/ml) | 450 | 400 | 350 | 300 | 250 | 200 | 150
|  | 49% HF Etch Particle Counts POP (20 nm/ml) | 45 | 40 | 35 | 30 | 25 | 20 | 15
|  | Elemental Free Carbon | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | 29% NH4OH: Al, Na, K, Fe, Ni, Cu, Cr, Co, Ca, (Au, Ba, Cd, Mg, Mn, Mo, Pb, Pd, Pt, Ru, Sn, Ti, V, W, Zn) (POD, ppt) [21] [Cleaning Chemistry] | 60 | 50 | 40 | 60 | 50 | 40 | 40
|  | 29% NH4OH: Al, Na, K, Fe, Ni, Cu, Cr, Co, Ca, (Au, Ba, Cd, Mg, Mn, Mo, Pb, Pd, Pt, Ru, Sn, Ti, V, W, Zn) Supplier Cleaning Chemistry | 60 | 50 | 40 | 60 | 50 | 40 | 40
|  | 29% NH4OH: Total Anions (ppb) | 10 | 10 |  | 10 | 10
|  | 29% NH4OH: % Assay Variance [51] POP [Cleaning Chemistry] | 0.85 | 0.85 | 0.85 | 0.8 | 0.75 | 0.75 | 0.75
|  | 29% NH4OH: Particle counts Supplier (20 nm / ml) [Cleaning Chemistry] | 450 | 400 | 350 | 300 | 250 | 200 | 150
|  | 29% NH4OH: Particle counts POP (20 nm /ml) [Cleaning Chemistry] | 45 | 40 | 35 | 30 | 25 | 20 | 15
|  | 29% NH4OH Total Organics | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | % NH4OH Elemental Free Carbon | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | 100% IPA metals Al, As, Ba, Ca, Cd, Co, Cr, Cu, Fe, K, Li, Mg, Mn, Mo, Na, Ni, Pb, Sb, Sn, Sr, Ti, V, W, Zn + Pt- cleaning from supplier (ppt) | <10 | <5 | <1 | <0.1 | <0.09 | <0.08 | <0.07
|  | 100% IPA metals Al, As, Ba, Ca, Cd, Co, Cr, Cu, Fe, K, Li, Mg, Mn, Mo, Na, Ni, Pb, Sb, Sn, Sr, Ti, V, W, Zn + Pt - cleaning from POP(ppt) | <10 | <1 | <0.1 | <0.01 | <0.009 | <0.008 | <0.007
|  | 100% IPA cleaning High Molecular Wt organics (>=10 carbon atoms ppb) | 150 | 100 | 50 | 40 | 30 | 20 | 10
|  | 100% IPA cleaning Assay minimum POP | 99.94 | 99.94 | 99.95 | 99.96 | 99.97 | 99.98 | 99.99
|  | 100% IPA cleaning Assay minimum Supplier | 99.94 | 99.94 | 99.94 | 99.94 | 99.97 | 99.98 | 99.99
|  | Variance (+/-) | 0.02 | 0.02 | 0.02 | 0.015 | 0.013 | 0.012 | 0.01
|  | 100% IPA cleaning Particle counts POP (10 nm / ml) | <20 | <20 | <20 | <20 | <20 | <20 | <20
|  | 100% IPA cleaning Particle counts supplier (10 nm / ml) | <60 | <60 | <60 | <60 | <60 | <60 | <60
|  | Elemental Free Carbon | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | 100% IPA metals Al, As, Ba, Ca, Cd, Co, Cr, Cu, Fe, K, Li, Mg, Mn, Mo, Na, Ni, Pb, Sb, Sn, Sr, Ti, V, W, Zn + Pt -drying from supplier (ppt) | <10 | <5 | <1 | <0.1 | <0.09 | <0.08 | <0.07
|  | 100% IPA metals Al, As, Ba, Ca, Cd, Co, Cr, Cu, Fe, K, Li, Mg, Mn, Mo, Na, Ni, Pb, Sb, Sn, Sr, Ti, V, W, Zn + Pt - drying from POP (ppt) | <10 | <1 | <0.1 | <0.01 | <0.009 | <0.008 | <0.007
|  | 100% IPA drying High Molecular Wt organics (>=10 carbon, BP>82) | 150 | 100 | 50 | 40 | 30 | 20 | 10
|  | 100% IPA drying Assay minimum POP (%) | 99.999 | 99.999 | 99.999 | 99.999 | 99.999 | 99.999 | 99.999
|  | 100% IPA drying Assay minimum Supplier (%) | 99.999 | 99.999 | 99.999 | 99.999 | 99.999 | 99.999 | 99.999
|  | 100% IPA drying Particle counts POP (10 nm / ml) | <20 | <20 | <20 | <20 | <20 | <20 | <20
|  | 100% IPA drying Particle counts supplier (10 nm / ml) | <60 | <60 | <60 | <60 | <60 | <60 | <60
|  | Elemental Free Carbon | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | 30% H2O2 Al, As, Ba, Ca, Cd, Co, Cr, Cu, Fe, K, Li, Mg, Mn, Mo, Na, Ni, Pb, Sb, Sn, Sr, Ti, V, W, Zn + Pt* (ppt, each) from supplier | 10 | 10 | 10 | 5 | 5 | 5 | 5
|  | 30% H2O2 Al, As, Ba, Ca, Cd, Co, Cr, Cu, Fe, K, Li, Mg, Mn, Mo, Na, Ni, Pb, Sb, Sn, Sr, Ti, V, W, Zn + Pt* (ppt, each) from POP | 10 | 10 | 10 | 5 | 5 | 5 | 5
|  | 30%H2O2 Silicon (ppt) | 500 | 500 | 500 | 500 | 400 | 300 | 250
|  | 30% H2O2: Anions (ppb) phosphates, sulfates, chloride | 7 | 7 | 7 | 7 | 6 | 5 | 5
|  | 30% H2O2: Anions (ppb) nitrate | 14 | 14 | 14 | 14 | 12 | 10 | 10
|  | 30% H2O2: resin byproducts (ppb) e.g. total amines | 2 | 2 | 2 | 2 | 1 | 1 | 1
|  | 30% H2O2: % Assay Variance [51] POP [Functional Chemistry] | 1.7 | 1.6 | 1.5 | 1.7 | 1.6 | 1.5 | 1.5
|  | 30% H2O2: Particle counts Supplier (20 nm /ml) [Functional Chemistry] | 500 | 450 | 400 | 350 | 300 | 250 | 200
|  | 30% H2O2: Particle counts (20nm, #/ml) POP [Functional Chemistry] | 50 | 45 | 40 | 35 | 30 | 25 | 20
|  | 30% H2O2 Elemental Carbon | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | 30% H2O2 organics, e.g. silicone (by nmr) and others (ppm) | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | 37% HCl as cleaning chemistry: Al, As, Ba, Ca, Cd, Co, Cr, Cu, Fe, K, Li, Mg, Mn, Mo, Na, Ni, Pb, Sb, Sn, Sr, Ti, V, W, Zn + Pt* (ppt, each) from supplier | 60 | 50 | 40 | 40 | 40 | 40 | 40
|  | 37% HCl: Al, As, Ba, Ca, Cd, Co, Cr, Cu, Fe, K, Li, Mg, Mn, Mo, Na, Ni, Pb, Sb, Sn, Sr, Ti, V, W, Zn + Pt* (ppt, each) from POP | 60 | 50 | 40 | 40 | 40 | 40 | 40
|  | 37% HCl: Anions (ppb) | 100 | 50 | 50 | 100 | 50 | 50 | 50
|  | 37% HCl: % Assay Variance [51] POP [Functional Chemistry] | 0.85 | 0.8 | 0.75 | 0.85 | 0.8 | 0.75 | 0.75
|  | 37% HCl: Particle counts Supplier (50 nm / ml) [Functional Chemistry] | 750 | 600 | 500 | 450 | 400 | 350 | 300
|  | 37% HCl: Particle counts POP (50 nm / ml) [Functional Chemistry] | 75 | 60 | 50 | 45 | 40 | 35 | 30
|  | 37% HCl Elemental Free Carbon | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | 96% H2SO4: Al, As, Ba, Ca, Cd, Co, Cr, Cu, Fe, K, Li, Mg, Mn, Mo, Na, Ni, Pb, Sb, Sn, Sr, Ti, V, W, Zn + Pt* (ppt, each) from supplier | 60 | 60 | 60 | 60 | 50 | 40 | 40
|  | 96% H2SO4: Al, As, Ba, Ca, Cd, Co, Cr, Cu, Fe, K, Li, Mg, Mn, Mo, Na, Ni, Pb, Sb, Sn, Sr, Ti, V, W, Zn + Pt* (ppt, each) from POP | 60 | 60 | 60 | 60 | 50 | 40 | 40
|  | 96% H2SO4: Anions (ppb) | 50 | 50 | 50 | 50 | 50 | 50 | 50
|  | 96% H2SO4: Anions (ppb) | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  | 96% H2SO4: % Assay Variance POP (% volume) [Functional Chemistry] | 0.85 | 0.85 | 0.85 | 0.85 | 0.8 | 0.75 | 0.75
|  | 96% H2SO4: Particle counts Supplier (20 nm / ml) [Cleaning Chemistry] | 500 | 450 | 400 | 350 | 300 | 250 | 200
|  | 96% H2SO4: Particle counts POP (20 nm /ml) [Cleaning Chemistry] | 50 | 45 | 40 | 35 | 30 | 25 | 20
|  | 96% H2SO4: Total Organics of UPW water for formulation | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | 96 % H2SO4 organics, e.g. silicone(by nmr) and others | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | 96% H2SO4Elemental Free Carbon | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | CMP slurries: scratching particles (#/ml >95% of largest mode + 10nm) Supplier (#/ml) | 120 | 120 | 120 | 120 | 100 | 80 | 80 | For Multi-Modal abrasives, values are based on the 95% of largest mode + 10nm. This is to measure the amount agglomeration that cause scratch defects during the CMP process.
|  | CMP slurries: scratching particles (#/ml >95% of largest mode + 10nm) POD (#/ml) | 60 | 60 | 60 | 60 | 50 | 40 | 40 | For Multi-Modal abrasives, values are based on the 95% of largest mode + 10nm. This is to measure the amount agglomeration that cause scratch defects during the CMP process. Raw slurries need to be controlled and then dilution and filtration of the diluted slurry need to be controlled
|  | CMP slurries: scratching particles (#/ml >95% of largest mode + 10nm) POU (#/ml) | 30 | 30 | 30 | 30 | 25 | 20 | 20 | After Final polishing process
CMP UPW used for dilution needs to match UPW roadmap in all respects
|  | CMP Slurries age of material | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | CMP Slurries Temperature | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | CMP Slurries Suspension | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | Post-CMP clean chemicals: particles >0.065 µm (#/ml) [1] [9] [17] [49] POD Non-Surfactant Based [Cleaning Chemistry] PROACTIVE: Non-EAP Particle Control: 50nm (#/L) | <140 | <140 | <140 | <140 | <140 | <140 | <140 | Chemistry containing Micelles will require a larger particle size threshhold to be used to prevent counting Micelles as harmfull particles.
|  | Post-CMP clean chemicals: particles >0.2 µm (/ml) [1] [9] [17] [49] Surfactant Based | 60 | 60 |  | 60 | 60 |  |  | Chemistry containing Micelles will require a larger particle size threshhold to be used to prevent counting Micelles as harmfull particles.
|  | Plating chemicals: particles > critical size (>150 nm) (#/ml) [1] [9] [17] [50] [Functional Chemistry] | 800 | 750 | 700 | 800 | 750 | 700 | 700 | Chemistry containing Micelles will require a larger particle size threshhold to be used to prevent counting Micelles as harmfull particles.
|  | Plating chemicals: purity | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | General Cleaning chemistries or blends: Al, Na, K, Fe, Ni, Cu, Cr, Co, Ca, (Au, Ba, Cd, Mg, Mn, Mo, Pb, Pd, Pt, Ru, Sn, Ti, V, W, Zn) Supplier Cleaning Chemistry (ppt) | 60 | 60 | 60 | 60 | 50 | 40 | 40
|  | General Cleaning chemistries or blends: Al, Na, K, Fe, Ni, Cu, Cr, Co, Ca, (Au, Ba, Cd, Mg, Mn, Mo, Pb, Pd, Pt, Ru, Sn, Ti, V, W, Zn) POP Cleaning Chemistry (ppt) | 60 | 60 | 60 | 60 | 50 | 40 | 40
|  | General Cleaning chemistries or blends: Total Anions (ppb) | 300 | 250 | 200 | 200 | 200 | 200 | 200
|  | General Cleaning chemistries or blends Particle counts Supplier (20 nm / ml) [Cleaning Chemistry] | 500 | 450 | 400 | 350 | 300 | 250 | 200 | Particles excluding light scattering artifacts
|  | General Cleaning chemistries or blends Particle counts POP (20 nm /ml) [Cleaning Chemistry] | 50 | 45 | 40 | 35 | 30 | 25 | 20 | Particles excluding light scattering artifacts
|  | General Cleaning chemistries or blends: Total Organics | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | General Cleaning chemistries or blends: Elemental Free Carbon | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | Propritary Chemistries and blends: Al, Na, K, Fe, Ni, Cu, Cr, Co, Ca, (Au, Ba, Cd, Mg, Mn, Mo, Pb, Pd, Pt, Ru, Sn, Ti, V, W, Zn) Supplier (ppt) | 60 | 60 | 60 | 60 | 50 | 40 | 40
|  | Propritary Chemistries and blends:Al, Na, K, Fe, Ni, Cu, Cr, Co, Ca, (Au, Ba, Cd, Mg, Mn, Mo, Pb, Pd, Pt, Ru, Sn, Ti, V, W, Zn) POP (ppt) | 60 | 60 | 60 | 60 | 50 | 40 | 40
|  | Propritary Chemistries and blends:: Total Anions (ppb) | 300 | 250 | 200 | 200 | 200 | 200 | 200
|  | Propritary Chemistries and blends:Particle counts Supplier (20 nm / ml) | 750 | 600 | 500 | 450 | 400 | 350 | 300 | Particles excluding light scattering artifacts
|  | Prioritary Chemistries and blends: Particle counts POP (20 nm / ml) | 75 | 60 | 50 | 45 | 40 | 35 | 30 | Particles excluding light scattering artifacts
|  | Propritary Chemistries and blends:Total Organics | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | Propritary Chemistries and blends:Elemental Free Carbon | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | Critical Cleans Al, As, Ba, Ca, Cd, Co, Cr, Cu, Fe, K, Li, Mg, Mn, Mo, Na, Ni, Pb, Sb, Sn, Sr, Ti, V, W, Zn + Pt from supplier (ppt) | 20 | 20 | 20 | 10 | 10 | 10 | 10 | **For GAA These will be re-evaluated and adjustmented when these processes get defined better
|  | Critical Cleans metals Al, As, Ba, Ca, Cd, Co, Cr, Cu, Fe, K, Li, Mg, Mn, Mo, Na, Ni, Pb, Sb, Sn, Sr, Ti, V, W, Zn + Pt POP etch (ppt) | 20 | 20 | 10 | 5 | 5 | 5 | 5 | **For GAA These will be re-evaluated and adjustmented when these processes get defined better
|  | Critical Cleans Anions (ppt) | 300 | 250 | 200 | 100 | 100 | 100 | 100
|  | Critical Cleans Cl (ppb) | 60 | 50 | 40 | 40 | 40 | 40 | 40
|  | Critical Cleans Each component in the blend Assay Variance (%vol) | 0.05 | 0.05 | 0.05 | 0.02 | 0.02 | 0.01 | 0.01 | **For GAA These will be re-evaluated and adjustmented when these processes get defined better
|  | Critical Cleans Particle Counts Supplier (20 nm / ml) | 500 | 450 | 400 | 350 | 300 | 250 | 200
|  | Critical Cleans Particle Counts POP (3.5 nm / ml) | 500 | 450 | 400 | 350 | 300 | 250 | 200 | **For GAA These will be re-evaluated and adjustmented when these processes get defined better
|  | Critical Cleans Organics ( 10 carbon ppb) | 150 | 100 | 50 | 40 | 30 | 20 | 10 | **For GAA These will be re-evaluated and adjustmented when these processes get defined better
|  | Critical Cleans: UPW organics | TBD | TBD | TBD | TBD | TBD | TBD | TBD | **For GAA These will be re-evaluated and adjustmented when these processes get defined better
|  | Critical Cleans: Elemental Free Carbon | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | Critical Cleans: oxygen or other gases | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | Developer TMAH Based:Al, As, Ba, Ca, Cd, Co, Cr, Cu, Fe, K, Li, Mg, Mn, Mo, Na, Ni, Pb, Sb, Sn, Sr, Ti, V, W, Zn + Pt from supplier (ppt) | 40 | 40 | 40 | 35 | 35 | 30 | 30
|  | Developer TMAH based: metals Al, As, Ba, Ca, Cd, Co, Cr, Cu, Fe, K, Li, Mg, Mn, Mo, Na, Ni, Pb, Sb, Sn, Sr, Ti, V, W, Zn + Pt POP (ppt) | 40 | 40 | 40 | 35 | 35 | 30 | 30
|  | Developer TMAH based: Anions (ppb) | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  | Developers TMAH based: Assay Variance (% vol) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
|  | Developers TMAH based: Particle Counts Supplier (20 nm / ml) | 500 | 450 | 400 | 350 | 300 | 250 | 200
|  | Developer TMAH based:Particle Counts POP (3.5 nm / ml) | 500 | 450 | 400 | 350 | 300 | 250 | 200
|  | Developer TMAH based: Organics (10 carbon ppb) | 150 | 100 | 50 | 40 | 30 | 20 | 10
|  | Developer TMAH based: Urea - fishhook defects (ppb) | 20 | 20 | 20 | 20 | 10 | 10 | 10
|  | Developer TMAH based: water content varience (ppb +-) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
|  | Developer TMAH based:viscosity | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | Developer TMAH based: Raw material shelf life (years <) | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  | Developer TMAH based: Elemental Free Carbon | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | Developer EUV: Al, As, Ba, Ca, Cd, Co, Cr, Cu, Fe, K, Li, Mg, Mn, Mo, Na, Ni, Pb, Sb, Sn, Sr, Ti, V, W, Zn + Pt from supplier (ppt) | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | Developer EUV: metals Al, As, Ba, Ca, Cd, Co, Cr, Cu, Fe, K, Li, Mg, Mn, Mo, Na, Ni, Pb, Sb, Sn, Sr, Ti, V, W, Zn + Pt POP (ppt) | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | Developer EUV: Anions (ppb) | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | Developer EUV: Assay Variance (%vol) | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | Developer EUV: Particle Counts Supplier (20 nm/ ml) | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | Developer EUV: Particle Counts POP (3.5 nm / ml) | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | Developer EUV: Organics (10 carbon ppb) | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | Developer EUV: Urea - fishhook defects (ppb) | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | Developer EUV: water content varience (ppb +-) | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | Developer EUV: viscosity | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | Developer EUV: Raw material shelf life (years <) | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | Developer EUV: Elemental Free Carbon | TBD | TBD | TBD | TBD | TBD | TBD | TBD
|  | Proprietary etch blends metals Al, As, Ba, Ca, Cd, Co, Cr, Cu, Fe, K, Li, Mg, Mn, Mo, Na, Ni, Pb, Sb, Sn, Sr, Ti, V, W, Zn + Pt from supplier (ppt) | 20 | 20 | 20 | 20 | 20 | 20 | 10
|  | Proprietary etch blends metals Al, As, Ba, Ca, Cd, Co, Cr, Cu, Fe, K, Li, Mg, Mn, Mo, Na, Ni, Pb, Sb, Sn, Sr, Ti, V, W, Zn + Pt POP etch (ppt) | 20 | 20 | 20 | 20 | 20 | 20 | 10
|  | Proprietary etch blend Assay Variance (%vol) | 0.5 | 0.5 | 0.5 | 0.2 | 0.2 | 0.1 | 0.1
|  | Proprietary Etch Blend Particle Counts Supplier (20 nm/ml) | 2000 | 2000 | 2000 | 1500 | 1500 | 1250 | 1250 | ** May not apply to blends that include surfactants or other components that will affect this number
Bulk Gases (Contaminants, ppbv) [5]
IS |  | Number of particles > critical size (/M3) | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
IS |  | Number of particles > 0.1 µm (/M3) | 100 | 100 | 100 | 100 | 100 | 100 | 100
IS | 3. Change in value or units of the parameter | N2 (O2, H2, H2O, CO, CO2, ≤C4, ≥C5) [34] | < 1…<10 | < 1…<10 | < 1…<10 | < 1…<10 | < 1…<10 | < 1…<10 | < 1…<10 | Post purification spec
IS | 1. No change | O2 (N2) | <50 | <50 | <50 | <50 | <50 | <50 | <50 |  | Nitride formation during deposition
IS | 1. No change | O2 (Ar) | <500 | <500 | <500 | <500 | <500 | <500 | <500 | As delivered when required. | Roughness during deposition
IS | 3. Change in value or units of the parameter | O2 (H2, H2O, CO, CO2, ≤C4, ≥C5) | < 1…<10 | < 1…<10 | < 1…<10 | < 1…<10 | < 1…<10 | < 1…<10 | < 1…<10 | no change to outlet spec
IS | 3. Change in value or units of the parameter | Ar (O2, H2, H2O, CO, CO2, ≤C4, ≥C5) [34] | < 1…<10 | < 1…<10 | < 1…<10 | < 1…<10 | < 1…<10 | < 1…<10 | < 1…<10 | Post purification spec
IS | 3. Change in value or units of the parameter | H2 (N2) | <1 | <1 | <1 | <1 | <1 | <1 | <1 | Post purification spec, when required
IS | 3. Change in value or units of the parameter | H2 (O2, H2O, CO, CO2, ≤C4, ≥C5) | < 1…<10 | < 1…<10 | < 1…<10 | < 1…<10 | < 1…<10 | < 1…<10 | < 1…<10 | Post purification spec
Is | 3. Change in value or units of the parameter | He (O2, H2, H2O, CO, CO2, ≤C4, ≥C5) [34] | < 1…<10 | < 1…<10 | < 1…<10 | < 1…<10 | < 1…<10 | < 1…<10 | < 1…<10 | Post purification spec
IS | 3. Change in value or units of the parameter | CO2 (CO, H2O, O2, ≤C4, ≥C5) | < 1…<10 | < 1…<10 | < 1…<10 | < 1…<10 | < 1…<10 | < 1…<10 | < 1…<10 | Post purification spec
NEW |  | CO2 (N2) | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | Post purification spec
NEW |  | CO2 (COS, CS2,H2S) | <1 | <1 | <1 | <1 | <1 | <1 | <1 | Post purification spec
NEW |  | CO2 (Total volatile acids (as SO2) | <1pptv | <1pptv | <1pptv | <1pptv | <1pptv | <1pptv | <1pptv | Post purification spec
NEW |  | CO2 (NH3) | <5pptv | <5pptv | <5pptv | <5pptv | <5pptv | <5pptv | <5pptv | Post purification spec
Lithography and Critical Metrology Purge Gases (ppbv)
Critical clean dry air
IS | 1. No change | Critical clean dry air (Each refractory compound (Organics containing S, P, Si) | <0.1 | <0.1 | <0.1 | <0.1 | <0.1 | <0.1 | <0.1
IS | 1. No change | Critical clean dry air (H2, CO) | <2000 | <2000 | <2000 | <2000 | <2000 | <2000 | <2000
IS | 1. No change | Critical clean dry air (H2O) | <1000 | <1000 | <1000 | <1000 | <1000 | <1000 | <1000
IS | 1. No change | Critical clean dry air (NH3 (as NH3)) | <0.1 | <0.1 | <0.1 | <0.1 | <0.1 | <0.1 | <0.1
IS | 1. No change | Critical clean dry air (organics (molecular weight > benzene) normalized to hexadecane equivalent) | <3 | <3 | <3 | <3 | <3 | <3 | <3
IS | 1. No change | Critical clean dry air (SO4 (as SO4)) | <0.03 | <0.03 | <0.03 | <0.03 | <0.03 | <0.03 | <0.03
IS | 1. No change | Critical clean dry air (total acid including SO2 (as SO4)) | <0.1 | <0.1 | <0.1 | <0.1 | <0.1 | <0.1 | <0.1
IS | 1. No change | Critical clean dry air (total base as NH3) | <1 | <1 | <1 | <1 | <1 | <1 | <1
Lithography nitrogen tool/ maintenance purging gas supply
IS | 1. No change | Lithography nitrogen tool/maintenance purging gas supply (H2O, O2, CO2) | <500 | <500 | <500 | <500 | <500 | <500 | <500
IS | 1. No change | Lithography nitrogen tool/maintenance purging gas supply (H2) | <2000 | <2000 | <2000 | <2000 | <2000 | <2000 | <2000
IS | 1. No change | Lithography nitrogen tool/maintenance purging gas supply (CO) | <2000 | <2000 | <2000 | <2000 | <2000 | <2000 | <2000
IS | 1. No change | Lithography nitrogen tool/maintenance purging gas supply (organics (molecular weight > benzene) normalized to hexadecane equivalent) | <3 | <3 | <3 | <3 | <3 | <3 | <3
IS | 1. No change | Lithography nitrogen tool/maintenance purging gas supply (total base (as NH3)) | <0.15 | <0.15 | <0.15 | <0.15 | <0.15 | <0.15 | <0.15
IS | 1. No change | Lithography nitrogen tool/maintenance purging gas supply (total acid (as SO4) including SO2) | <0.025 | <0.025 | <0.025 | <0.025 | <0.025 | <0.025 | <0.025
IS | 1. No change | Lithography nitrogen tool/maintenance purging gas supply (refractory compounds (organics containing S, P, Si, etc.) normalized to hexadecane equivalent) | <0.1 | <0.1 | <0.1 | <0.1 | <0.1 | <0.1 | <0.1
Lithography hydrogen tool/ maintenance purging gas supply
IS | 1. No change | Lithography hydrogen tool/maintenance purging gas supply (H2O) | < 1 | < 1 | < 1 | < 1 | < 1 | < 1 | < 1
IS | 1. No change | Lithography hydrogen tool/maintenance purging gas supply (O2) | < 0.25 | < 0.25 | < 0.25 | < 0.25 | < 0.25 | < 0.25 | < 0.25
IS | 1. No change | Lithography hydrogen tool/maintenance purging gas supply (CO) | < 1 | < 1 | < 1 | < 1 | < 1 | < 1 | < 1
IS | 1. No change | Lithography hydrogen tool/maintenance purging gas supply (CO2) | < 0.25 | < 0.25 | < 0.25 | < 0.25 | < 0.25 | < 0.25 | < 0.25
IS | 1. No change | Lithography hydrogen tool/maintenance purging gas supply (Organics (molecular weight > benzene) normalized to hexadecane equivalent) | < 1 | < 1 | < 1 | < 1 | < 1 | < 1 | < 1
IS | 1. No change | Lithography hydrogen tool/maintenance purging gas supply (CxHy (45-100 amu)) | < 0.2 | < 0.2 | < 0.2 | < 0.2 | < 0.2 | < 0.2 | < 0.2
IS | 1. No change | Lithography hydrogen tool/maintenance purging gas supply (CxHy (>100 amu) - Condensable) | < 0.002 | < 0.002 | < 0.002 | < 0.002 | < 0.002 | < 0.002 | < 0.002
IS | 1. No change | Lithography hydrogen tool/maintenance purging gas supply (Total S components) | TBD | TBD | TBD | TBD | TBD | TBD | TBD
IS | 1. No change | Lithography hydrogen tool/maintenance purging gas supply (Each refractory compound (0rganics containing S, P, Si) ) | < 0.001 | < 0.001 | < 0.001 | < 0.001 | < 0.001 | < 0.001 | < 0.001
Etchants (Corrosive, e.g., BCl3, Cl2, HBr)
IS | 1. No change | O2, H2O (ppbv) | <500 | <500 | <500 | <500 | <500 | <500 | <500
IS | 1. No change | Critical specified metals/total metals (ppbw) [19] | <1/1000 | <1/1000 | <1/1000 | <1/1000 | <1/1000 | <1/1000 | <1/1000
Etchants (Non-corrosive, e.g., C5F8, C4F8, C4F6, CH2F2, SF6)
IS | 1. No change | O2, H2O (ppbv) | <1000 | <1000 | <1000 | <1000 | <1000 | <1000 | <1000
Etchants (e.g. Xe)
IS | 1. No change | O2, H2O (ppbv) | <1000 | <1000 | <1000 | <1000 | <1000 | <1000 | <1000
ALD/CVD blanket / purge/ delivery gases
IS | 1. No change | Sweep and bubbler gases for ALD/CVD volatile chemical delivery e.g., N2 (O2, H2, H2O, CO, CO2, THC) (ppb) [34] | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | Gapfill -W
NEW |  | WF6 - Assay | >99.7 | >99.7 | >99.7 | >99.7 | >99.7 | >99.7 | >99.7
NEW |  | WF6 - Metals each element (ppb) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | WF6 - O2 ppm | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | Gapfill Ru
NEW |  | Ru(EtCp)2 - Assay | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | Barrier/ Liner Cu (Ta/TaN)
NEW |  | PDMAT - Assay | >99.8 | >99.8 | >99.8 | >99.8 | >99.8 | >99.8 | >99.8
NEW |  | PDMAT - Metals each element (ppb) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | PDMAT - Nb (ppm) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | PDMAT - H2O (ppm) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | PDMAT - O2 ppm | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | PDMAT - Hydrocarbons ppm | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | PDMAT - Chloride ppm | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | PDMAT - Hydroloysis product (alkylamine) ppm | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TBTEMT - Assay | >99.11 | >99.11 | >99.11 | >99.11 | >99.11 | >99.11 | >99.11
NEW |  | TBTEMT - Metals each element (ppb) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TBTEMT - Nb ppm | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TBTEMT - H2O ppm | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TBTEMT - O2 ppm | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TBTEMT - Hydrocarbons ppm | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | Barrier/ Liner W->Mo (TiN)
NEW |  | TiCl4 - Assay | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TiCl4 - Metals each element (ppb) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TiCl4 - H2O ppm | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TiCl4 - O2 ppm | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TiCl4 - Hydrocarbons ppm | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TDMAT - Assay | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TDMAT - Metals each element (ppb) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TDMAT - H2O ppm | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TDMAT - O2 ppm | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TDMAT - Hydrocarbons ppm | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TDEAT - Assay | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TDEAT - Metals each element (ppb) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TDEAT - H2O ppm | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TDEAT - O2 ppm | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TDEAT - Hydrocarbons ppm | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | Barrier/ Liner Nb
NEW |  | TBTDEN - Assay | >99.9 | >99.9 | >99.9 | >99.9 | >99.9 | >99.9 | >99.9
NEW |  | TBTDEN - Metals each element (ppb) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TBTDEN - H2O ppm | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TBTDEN - O2 ppm | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TBTDEN - Hydrocarbons ppm | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TBTDEN - Chloride ppm | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TBTDEN - Hydroloysis product (alkylamine) ppm | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TEMAT - Assay | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TEMAT - H2O ppm | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TEMAT - O2 ppm | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TEMAT - Hydrocarbons ppm | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | Etch Stop (AlN) Al
NEW |  | TMA - Assay | 99.5 | 99.5 | 99.5 | 99.5 | 99.5 | 99.5 | 99.5
NEW |  | TMA - Metals each element (ppb) | <150 | <150 | <150 | <150 | <150 | <150 | <150
NEW |  | TMA - O2 ppm | <10 | <10 | <10 | <10 | <10 | <10 | <10
NEW |  | TMA - Silicon ppm | <1 | <1 | <1 | <1 | <1 | <1 | <1
NEW |  | TMA - Hydrocarbons ppm | <5 | <5 | <5 | <5 | <5 | <5 | <5
NEW |  | TDEAA - Assay | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TEA - Assay | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | HighK dielectric Hf
NEW |  | HfCl4 - Assay | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | HfCl4 - Metals each element (ppb) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | HfCl4 - Zr (ppm) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | HfCl4 - Hydrocarbons ppm | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | HfCl4 - Hydroloysis product Hf oxides ppm | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TEMAHf - Assay | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | HTB Octane / HTTB - Assay | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TDEAH - Assay | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TDEAH - Organic Porogen (%) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TDEAH - Metals each element (ppb) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TDEAH - Total metals (ppbw) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TDEAH - Zr (ppm) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TDEAH - Hydrocarbons (% by NMR) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TDEAH - Chloride ppm | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TDEAH - Hydroloysis product (alkylamine) ppm | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | HighK dielectric ZrOx
NEW |  | ZrCl4, TDMAZ - Assay | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TDEAZ - Assay | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | La(FMD)3 - Assay | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | Mg(EtCp)2 - Assay | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | LowK Main backbone/
NEW |  | DEMS - Assay | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | DEMS - Organic Porogen (%) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | DEMS - Metals except B, Au, Ag (ppb, each) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | DEMS - B, Au, Ag (ppb, each) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | DEMS - H2O (ppm) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | DEMS - CO, CO2 (ppm) | <0.7 | <0.7 | <0.7 | <0.7 | <0.7 | <0.7 | <0.7
NEW |  | DEMS - Ar+O2 (ppm) | <0.7 | <0.7 | <0.7 | <0.7 | <0.7 | <0.7 | <0.7
NEW |  | DEMS - NMHC C2-C4 (ppm) | <4 | <4 | <4 | <4 | <4 | <4 | <4
NEW |  | DEMS - N2 (ppm) | <2 | <2 | <2 | <2 | <2 | <2 | <2
NEW |  | DEMS - Chloride (ppm) | <4 | <4 | <4 | <4 | <4 | <4 | <4
NEW |  | DMDMOS - Assay | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | DMDMOS - Metals except B, Au, Ag (ppb, each) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | DMDMOS - B, Au, Ag (ppb, each) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | DMDMOS - H2O (ppm) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | DMDMOS - CO, CO2 (ppm) | <0.9 | <0.9 | <0.9 | <0.9 | <0.9 | <0.9 | <0.9
NEW |  | DMDMOS - Ar+O2 (ppm) | <0.9 | <0.9 | <0.9 | <0.9 | <0.9 | <0.9 | <0.9
NEW |  | DMDMOS - NMHC C2-C4 (ppm) | <4 | <4 | <4 | <4 | <4 | <4 | <4
NEW |  | DMDMOS - N2 (ppm) | <2 | <2 | <2 | <2 | <2 | <2 | <2
NEW |  | DMDMOS - Chloride (ppm) | <6 | <6 | <6 | <6 | <6 | <6 | <6
NEW |  | TMCTS - Assay | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | OMCTS - Assay | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | OMCTS - Metals except B, Au, Ag (ppb, each) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | OMCTS - B, Au, Ag (ppb, each) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | OMCTS - H2O (ppm) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | OMCTS - CO, CO2 (ppm) | <0.8 | <0.8 | <0.8 | <0.8 | <0.8 | <0.8 | <0.8
NEW |  | OMCTS - Ar+O2 (ppm) | <0.8 | <0.8 | <0.8 | <0.8 | <0.8 | <0.8 | <0.8
NEW |  | OMCTS - NMHC C2-C4 (ppm) | <4 | <4 | <4 | <4 | <4 | <4 | <4
NEW |  | OMCTS - N2 (ppm) | <2 | <2 | <2 | <2 | <2 | <2 | <2
NEW |  | OMCTS - Chloride (ppm) | <5 | <5 | <5 | <5 | <5 | <5 | <5
NEW |  | SiO2 Main backbone/
NEW |  | 3MS - Assay | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | 3MS - Metals except B, Au, Ag (ppb, each) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | 3MS - B, Au, Ag (ppb, each) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | 3MS - H2O (ppm) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | 3MS - CO, CO2 (ppm) | <0.6 | <0.6 | <0.6 | <0.6 | <0.6 | <0.6 | <0.6
NEW |  | 3MS - Ar+O2 (ppm) | <0.6 | <0.6 | <0.6 | <0.6 | <0.6 | <0.6 | <0.6
NEW |  | 3MS - NMHC C2-C4 (ppm) | <4 | <4 | <4 | <4 | <4 | <4 | <4
NEW |  | 3MS - N2 (ppm) | <2 | <2 | <2 | <2 | <2 | <2 | <2
NEW |  | 3MS - Chloride (ppm) | <3 | <3 | <3 | <3 | <3 | <3 | <3
NEW |  | 4MS - Assay | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | BTBAS - Assay | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | TDMAS / 3DMAS - Assay | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | 4DMAS - Assay | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | SiN Main backbone/
NEW |  | Ga(CH3)3 (TMG) - Assay | tbd | tbd | tbd | tbd | tbd | tbd | tbd
NEW |  | In(CH3)3 (TMI) - Assay | tbd | tbd | tbd | tbd | tbd | tbd | tbd
IS |  | Post Point of Use Purification
IS |  | POUF - SiH4, Si2H6, GeH4, process and purge H2, process and purge N2
IS | 1. No change | POUF - SiH4, Si2H6, GeH4 (O2 (ppb)) | <10 | <10 | <10 | <10 | <10 | <10 | <10
IS | 1. No change | POUF - SiH4, Si2H6, GeH4 (H2O (ppb)) | <20 | <20 | <20 | <20 | <20 | <20 | <20
IS | 1. No change | POUF - SiH4, Si2H6, GeH4 (Hydrocarbons (ppb)) | <20 | <20 | <20 | <20 | <20 | <20 | <20
IS |  | POUF - Deposition gases - GeH4 [7782-65-2]
IS | 1. No change | POUF - GeH4 (O2, H2O (ppbv)) | <10 | <10 | <10 | <10 | <10 | <10 | <10
IS | 1. No change | POUF - GeH4 (Other dopants (ppbv)) | <20 | <20 | <20 | <20 | <20 | <20 | <20
IS |  | Mixing tolerance for mixtures
IS |  | GeCl4 [10038-98-9] | tbd | tbd | tbd | tbd | tbd | tbd | tbd
IS |  | GeH4 [7782-65-2] | tbd | tbd | tbd | tbd | tbd | tbd | tbd
IS |  | SiH2Cl2 [4109-96-0] | tbd | tbd | tbd | tbd | tbd | tbd | tbd
IS |  | Si2H6 [1590-87-0] | tbd | tbd | tbd | tbd | tbd | tbd | tbd
IS |  | SiH4 [7803-62-5] | +/-1% | +/-1% | +/-1% | +/-1% | +/-1% | +/-1% | +/-1%
IS |  | Si2H6 [1590-87-0] | tbd | tbd | tbd | tbd | tbd | tbd | tbd
IS |  | Other available High purity volatile liquid precursors available for Electronic Thin film applications (General) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
IS |  | Deposition Gases CVD/PECVD/ ALD (General) (O2, H2O (ppbv)) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
IS |  | Deposition Gases CVD/PECVD/ ALD (General) (Critical specified metals/total metals (ppbw) )[19] | tbd | tbd | tbd | tbd | tbd | tbd | tbd
IS |  | Deposition Gases CVD/PECVD/ ALD (General) (Dopants (ppbv)) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
IS |  | Amorphous Carbon (Double Patterning) e.g., propylene [9003-07-0] and acetylene [74-86-2]
IS |  | Amorphous Carbon (Double Patterning) (Other hydrocarbons (ppmv)) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
IS |  | Amorphous Carbon (Double Patterning) (Total metals (ppbw)) | < 1000 | < 1000 | < 1000 | < 1000 | < 1000 | < 1000 | < 1000
IS |  | Deposition gases (e.g. NH3)
IS |  | Deposition gases (e.g. NH3) (O2, H2O (ppbv)) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
IS |  | Deposition gases (e.g. NH3) (Critical specified metals/total metals (ppbw)) [19] | tbd | tbd | tbd | tbd | tbd | tbd | tbd
IS |  | Deposition gases (e.g., N2O, NO)
IS |  | Deposition gases (e.g. N2O, NO) (O2, H2O (ppbv)) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
IS |  | Deposition gases (e.g. N2O, NO) (Critical specified metals/total metals (ppbw)) [19] | tbd | tbd | tbd | tbd | tbd | tbd | tbd
IS |  | Deposition gases - electrical dopants (e.g. AsH3, PH3, B2H6)
IS |  | Electrical dopants (O2, H2 (ppb)) [36] | tbd | tbd | tbd | tbd | tbd | tbd | tbd
IS |  | Other dopants (ppbv) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
IS |  | Other dopants (Mixing tolerance for mixtures (relative variance)) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
IS |  | Implant gases - AsH3, PH3, BF3
IS |  | Implant gases (O2, H2O (ppbv)) | <500 | <500 | <500 | <500 | <500 | <500 | <500
IS |  | Implant gases (Other dopants (ppbv)) | <1 | <1 | <1 | <1 | <1 | <1 | <1
IS |  | Implant gases (Mixing tolerance for F2 (relative variance)) | +/-4% | +/-4% | +/-4% | +/-4% | +/-4% | +/-4% | +/-4%
IS |  | Implant gases (Other constituents (ppbv)) | <25000 | <25000 | <25000 | <25000 | <25000 | <25000 | <25000
IS |  | Laser gases - Litho, (e.g. F2/Kr/Ne)
IS |  | Laser Gases (O2, H2O (ppbv)) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
| 1. No change | Critcal Components [45][46][48][51][52][55][58] [59][60][61][62][63] | [7 empty] | Focus is for HP polymer materials used in liquid delivery systems | Update SEMI F57
| 1. No change | HP materials used in distribution of UPW
IS | 3. Change in value or units of the parameter | Total organic carbon (ng/m2) Ambient UPW [47] [51] | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | baseline current performance of HP polymer materials in HUPW
| 2. New parameter line driven by technology risks or needs | Total Organics (ug/m2) HUPW [47] [51][54] | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | capability of currently used PVDF material for HUPW after 14 day rinse for new installations
IS | 3. Change in value or units of the parameter | Critical Organics as C (ug/m2) [62][61] [56] [64] |  | TBD | TBD | TBD | TBD | TBD | TBD | we do not have data on organics from CC. It is still being defined and testing for what ends up on wafer
| 1. No change | Non-critical organics as C (μg/m2) [22], | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | marginal capability of currently used PVDF material
| 2. New parameter line driven by technology risks or needs | Critical Organics as C (μg/m2) [61] [62], HUPW POC | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000
| 2. New parameter line driven by technology risks or needs | Non-critical organics as C (ug/m2) [22], HUPW POC | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000
| 1. No change | Critical particle size non-electrically active (non-EAP) (nm) based on 50% of Logic 1/2 Pitch (nm (contacted) [1] | 10 | 9 | 9 | 9 | 7 | 7 | 7
IS | 3. Change in value or units of the parameter | Number of non-EAP at critical size (#/m2) [26], POE | <500 | 450 | 400 | 350 | 300 | 250 | 250 | Non EAP. For additional information refer to UPW notes.
IS | 3. Change in value or units of the parameter | PROACTIVE: Non-EAP Particle Control: 30nm (#/m2), Feed to the Final Filter [26][52][56][59][60] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | Non EAP. For additional information refer to UPW notes. | Update SEMI F104
|  | Critical particle size (nm) of Electrically Active particles based on 50% width of fin Logic SiGe Front End or other device critical dimensions for LGAA (>2 monolayers) | 3.5 | 3 | 3 | 3 | 3.5 | 3.5 | 3.5 | based on input from MM
IS | 3. Change in value or units of the parameter | Number of EAP at critical size (#/m2) [26], POE | <50000 | 45000 | 40000 | 35000 | 30000 | 25000 | 25000 | Non EAP. For additional information refer to UPW notes.
IS | 3. Change in value or units of the parameter | PROACTIVE: EAP Particle Control: 30nm (#/m2), Feed to the Final Filter [26][52][56][59][60] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | Non EAP. For additional information refer to UPW notes. | Update SEMI F104
| 1. No change | Critical size (EUV mask), nm | 12 | 12 | 12 | 12 | 12 | 12 | 12
| 1. No change | Number of particles for EUV mask production (#/m2) [26.3], POE | <500 | 450 | 400 | 350 | 300 | 250 | 250
| 1. No change | Particle Precursors, #/m2 [56] High molecular weight organics | TBD | TBD | TBD | TBD | TBD | TBD | TBD
IS | 3. Change in value or units of the parameter | Metals (ug/m2) [51] (Al, As, Ba, Cd, Co, Cr, Cu, Fe, K, Li, Mg, Mn, Mo, Na, Ni, Pb, Sb, Sn, Sr, Ti, V, W, Zn) | <10 | <5 | <5 | <5 | <3 | <3 | <3 | baseline current performance of HP polymer materials
| 1. No change | B (ug/m2) [51] | <20 | <20 | <20 | <20 | <20 | <20 | <20 | baseline current performance of HP polymer materials
IS | 3. Change in value or units of the parameter | Critical Metals for image sensors (ug/m2 each) (Cu, Mn, Co) [39], POP |  |  | <2 | <2 | <2 | <2 | <2 |  | Cu 1, Mn 0.6, Co 0.4 detction limit
IS | 3. Change in value or units of the parameter | Critical Metals for image sensors (ug/m2 each) (W, Ti, Mo) |  | <0.5 | <0.5 | <0.5 | <0.5 | <0.5 | <0.5 |  | W 0.4, Ti, Mo 1.0 detection limit
| 1. No change | Anions (ug/m2) Cl , NO2, NO3, SO4 | <100 | <100 | <100 | <100 | <100 | <100 | <100 | baseline current performance of HP polymer materials
| 1. No change | PO4, (ug/m2) [51] | <85 | <85 | <85 | <85 | <85 | <85 | <85 | baseline current performance of HP polymer materials
| 1. No change | F (ug/m2) [51] ambient UPW | <350 | <350 | <350 | <350 | <350 | <350 | <350
IS | 3. Change in value or units of the parameter | F (ug/m2) [53] [54] HUPW | <1400 | <1400 | <1400 | <1400 | <1400 | <1400 | <1400 | curently used PVDF material with a 30 day rinse for new installations
| 1. No change | Critcal Components [45][46][48][51][52][55][58] [59][60][61][62][63]
| 1. No change | HP materials used in distribution of HP chemicals
| 2. New parameter line driven by technology risks or needs | Critical Cleans - blends
| 2. New parameter line driven by technology risks or needs | Critical Cleans metals Al, As, Ba, Ca, Cd, Co, Cr, Cu, Fe, K, Li, Mg, Mn, Mo, Na, Ni, Pb, Sb, Sn, Sr, Ti, V, W, Zn + Pt POP etch ug/m2 | < .031 | < .031 | <.015 | <.015 | <.015 | <.015 | <.015 | baseline current performance of HP polymer materials
| 2. New parameter line driven by technology risks or needs | Critical Cleans Anions ug/m2 | <0.046 | <0.046 | <0.046 | <0.046 | <0.046 | <0.046 | <0.046 | Based on extraction in UPW. We need data from crit clean chems.
| 2. New parameter line driven by technology risks or needs | Critical Cleans Cl ppt | <0.046 | <0.046 | <0.046 | <0.046 | <0.046 | <0.046 | <0.046
| 2. New parameter line driven by technology risks or needs | Critical Cleans Particle Counts POP 3.5 nm #/m2 | <7200 | <7200 | <7200 | <7200 | <7200 | <7200 | <7200
| 2. New parameter line driven by technology risks or needs | Critical Cleans Particle Counts POP 3.5 nm #/m2 | <7200 | 450 | 400 | 350 | 300 | <3600 | <3600
| 2. New parameter line driven by technology risks or needs | Critical Cleans Organics ppb 10 carbon compound ug/m2 | <.230 | <.150 | <.075 | <.06 | <.045 | <0.30 | <.015 |  |  | 0.023077
IS | 3. Change in value or units of the parameter | All cleaning chemistries (aqueous and solvent) Al, Ba, B, K, Na, K, Fe, Li, Mg, Mn, Pb, Sn, Ti, Zn, Ni, Cu, Cr, Co, (ug/m2, each) | < .031 | < .031 | < .031 | < .031 | < .031 | <0.015 | <0.015
| 1. No change | Acid and Caustic Delivery Systems Ca μg/m2 | <.015 | <.015 | <.015 | <.015 | <.015 | <.015 | <.015
IS | 3. Change in value or units of the parameter | 30% H2O2: Al, Na, K, Fe, Ni, Cu, Cr, Co, Ca, (Ag, Au, Ba, Cd, Mg, Mn, Mo, Pb, Pd, Pt, Ru, Sn, Ti, V, W, Zn) (ug/m2, each) [21] | <.076 | <.076 | <.076 | <.076 | < .031 | < .031 | < .031
| 2. New parameter line driven by technology risks or needs | 30% H2O2: Anions (ug/m2) phosphates, sulfates, chloride | <0.046 | <0.046 | <0.046 | <0.046 | < .031 | < .031 | < .031 | baseline current performance of HP polymer materials
| 2. New parameter line driven by technology risks or needs | 30% H2O2: Anions (ug/m2) nitrate | <.087 | <.087 | <.087 | <.087 | <0.06 | <0.06 | <0.06
| 2. New parameter line driven by technology risks or needs | 30% H2O2: Particle counts (20nm, #/m2) [52] POP [Functional Chemistry] | <3600 | <3600 | <3600 | <3600 | <3600 | <3600 | <3600 | baseline current performance of HP polymer materials
IS | 3. Change in value or units of the parameter | 100% IPA: Al, Ba, B, K, Na, K, Fe, Li, Mg, Mn, Pb, Sn, Ti, Zn, Ni, Cu, Cr, Co, Ca (ug/m2, each) | <0.008 | <0.003 | <0.003 | <0.003 | <0.003 | <0.003 | <0.003 | The new metals values in chem rd map are extrtemely low. We do not have data on extraction in IPA
IS | 3. Change in value or units of the parameter | 100% IPA: Ca (ug/m2) | tbd | tbd | tbd | tbd | tbd | tbd | tbd
IS | 3. Change in value or units of the parameter | 100% IPA: High molecular weight organics (ug/m2) | <0.45 | <0.45 | <0.45 | <0.45 | <0.45 | <0.45 | <0.45 | This is unkown at this time for organics from CC that meet this criteria.
| 1. No change | 100% IPA: Anions (ug/m2) | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | baseline current performance of HP polymer materials
| 2. New parameter line driven by technology risks or needs | 100% IPA cleaning High Molecular Wt organics > 10 carbons ug/m2 | <0.87 | <0.7 | <0.31 | <0.23 | <.15 | <.12 | <.09 | This is unkown at this time for organics from CC that meet this criteria.
| 2. New parameter line driven by technology risks or needs | 100% IPA cleaning Particle counts POP 10nm/m2 | <1150 | <1150 | <1150 | <1150 | <1150 | <1150 | <1150
IS | 3. Change in value or units of the parameter | Acid and Casutic Delivery metals ng/m2 (Al, As, Ba, Ca, Cd, Co, Cr, Cu, Fe, K, Li, Mg, Mn, Mo, Na, Ni, Pb, Sb, Sn, Sr, Ti, V, W, Zn) | <0.046 | <0.046 | <0.046 | <0.046 | < .031 | < .031 | < .031
IS | 3. Change in value or units of the parameter | 29% NH4OH: metals (ug/m2) Al, Na, K, Fe, Ni, Cu, Cr, Co, Ca, (Au, Ba, Cd, Mg, Mn, Mo, Pb, Pd, Pt, Ru, Sn, Ti, V, W, Zn) POP [21] Cleaning Chemistry | <0.046 | <0.046 | <0.046 | <0.046 | < .031 | < .031 | < .031
| 5. Deleted - parameter no longer required for the technology roadmap | Post-CMP clean chemicals: particles >0.2 µm (#/m2) Surfactant Based | TBD | TBD | TBD | TBD | TBD | TBD | TBD
IS |  | 1. No change
NEW |  | 3. Change in value or units of the parameter
4. Change in the parameter definition
5. Deleted - parameter no longer required for the technology roadmap
6. Deleted note or change to note
7. line copied or moved from another location in the table (not a new parameter)
Note on D254: Andreas Neuber: Assay in % by NMR
Note on E254: Andreas Neuber: Assay in % by NMR
Note on F254: Andreas Neuber: Assay in % by NMR
Note on G254: Andreas Neuber: Assay in % by NMR
Note on H254: Andreas Neuber: Assay in % by NMR
Note on I254: Andreas Neuber: Assay in % by NMR
Note on J254: Andreas Neuber: Assay in % by NMR
Note on D262: Andreas Neuber: Assay in % by NMR
Note on E262: Andreas Neuber: Assay in % by NMR
Note on F262: Andreas Neuber: Assay in % by NMR
Note on G262: Andreas Neuber: Assay in % by NMR
Note on H262: Andreas Neuber: Assay in % by NMR
Note on I262: Andreas Neuber: Assay in % by NMR
Note on J262: Andreas Neuber: Assay in % by NMR
Note on D274: Andreas Neuber: Assay in % by NMR
Note on D279: Andreas Neuber: Assay in % by NMR
Note on D285: Andreas Neuber: Assay in % by NMR
Note on E285: Andreas Neuber: Assay in % by NMR
Note on F285: Andreas Neuber: Assay in % by NMR
Note on G285: Andreas Neuber: Assay in % by NMR
Note on H285: Andreas Neuber: Assay in % by NMR
Note on I285: Andreas Neuber: Assay in % by NMR
Note on J285: Andreas Neuber: Assay in % by NMR
Note on C292: Andreas Neuber: tetrakis (ethylmethyl-amido) titanium
Note on D292: Andreas Neuber: Assay in % by NMR
Note on E292: Andreas Neuber: Assay in % by NMR
Note on F292: Andreas Neuber: Assay in % by NMR
Note on G292: Andreas Neuber: Assay in % by NMR
Note on H292: Andreas Neuber: Assay in % by NMR
Note on I292: Andreas Neuber: Assay in % by NMR
Note on J292: Andreas Neuber: Assay in % by NMR
Note on D310: Andreas Neuber: Assay by NMR
Note on C312: Andreas Neuber: Tetrakis(diethylamino)hafnium
Note on D312: Andreas Neuber: Assay by NMR
Note on C321: Andreas Neuber: Tetrakis(dimethylamino)zirconium(IV)
Note on C323: Andreas Neuber: (Lanthanum tris(N,N’-isopropylformamidinate)
Note on C367: Andreas Neuber: Tris(dimethylamino)silane
Note on C370: Andreas Neuber: Used in LED and Power CMOS
Note on C371: Andreas Neuber: Used in LED and power CMOS

## Notes for Table YE3
INDEX
Notes for Table YE3
[1] Logic was chosen to be a driver for Yield roadmap for the following reasons: • It has tighter pitch size • Flash is moving to 3D structure where the pitch equivalent is much larger • Logic has many more metal layers and higher complexity, increasing risks • Logic has less redundancy compared to Flash memory • Flash has self-alignment – none for logic Critical particle size is based on ½ pitch design rule for electrically active particles, assuming that "bridging" can be caused by particles smaller than the ½ pitch size. All other particles are not expected to become a device "killer" until their size exceeds ½ pitch.
[2] Airborne particle requirements are based on ISO 14644-1 at “at rest”.[3]
[3] Ion/species indicated is basis for calculation. Exposure time is 60 minutes with starting surface concentration of zero. Basis for lithography projections is defined by lithography tool suppliers. Metals and organics scale as defined in the surface preparation roadmap for metallics and organics. Values listed in table are based on experience, however, all airborne molecular contaminants can be calculated as S=E*(N*V/4); where S is the arrival rate (molecules/second/cm2), E is the sticking coefficient (between 0 and 1), N is the concentration in air (molecules/cm3); and V is the average thermal velocity (cm/second). The following sticking coefficients have been proposed; SO4 = 1x10 -5, NH3 = 1x10 -6, Cu = 2x10 -5. The sticking coefficients for organics vary greatly with molecular structure and are also dependent on surface termination.
[4] Includes P, B, As, Sb
[5] Contaminant targets apply up to POE (point-of-entry). POE is defined as the entry point to the equipment or subequipment, see also the text. Benchmark data has been collected both at Point of Delivery (POD) or Point of Entry (POE), which typically show only minor differences.
[6] Critical metals and ions may include: Al, As, Ba, Ca, Co, Cu, Cr, Fe, K, Li, Mg, Mn, Na, Ni, Pb, Sn, Ti, Zn. Three different case studies were reviewed where the levels of Ca, Fe, and Ni in the UPW resulted in levels of problem densities (atoms/sq cm) on the wafer. These were reduced to acceptable levels by reducing the level of these elements in the UPW to levels well below 10 ppt. In only one case does the data exist that showed success by obtaining values below 0.5 ppt. These results drive the 1.0 ~ 0.5 ppt values.
[7] Units on all contaminants in WECC Table are often given as ppb (or ppm or ppt, we use ppb here solely for demonstration purposes). The reader should be aware that these units of parts per billion (ppb) may be ppb by mass, volume, or molar ratios. Where not designated, the following guidelines apply: Chemicals and UPW are typically ppb by mass, while gases and clean room are typically ppb by volume. In the case of the fluid acting as an ideal gas, ppb by volume is equal to ppb molar. The notable exception to the above is metals in gases that are ppb by mass. In UPW, ppb is used based on mass of water. Since 1 liter of water equals ~1 kg, 1 ppb is equal to 1 µg/l. Some parameters in the tables may be considered process variables rather than contaminants in the classical meaning. They are marked by an asterisk. The limits are sometimes fluent.
[8] Detection of metals at the levels indicated will be dependent on sampling time and flow rate. Sticking Coefficients vary widely for metals. It is generally believed that Cu has a sticking coefficient 10x of other metals, and therefore the guideline for Cu could be lower.
[9] For Multi-Modal abrasives, values are based on the MPS of the largest Mode. This is to measure the amount agglomeration that cause scratch defects during the CMP process.
[10] The Dissolved Nitrogen range is solely for the physical process needs of megasonics cleaning. Processes without megasonics cleaning can ignore the line item. The concentration is process specific and needs to be determined by the end user. Factors to consider include UPW temperature, partial pressure in the gas phase and megasonic energy input at the tool. Other gases, such as oxygen and hydrogen, may be used with different optimum levels. Process enhancements through chemistry associated with the other gases or other chemicals are outside of the scope of this chapter. While a relatively wide range of dissolved nitrogen values may be acceptable based on other process variables it is important to note that tight control at the desired value is warranted. DN2 spec is considered at POE, taking into account possibility that N2 control inside the tool.
[11] As of the current year's update the finest production available sensitivity liquid particle sensor for chemicals is 0.040 µm, although measurement technology is being developed at 0.020 µm. Values obtained by these particle counters are not directly comparable to the roadmap values and need to be normalized to critical particle size values in the roadmap using the equation and methods of Footnote A above. Interim solution to higher sensitivity particle counter is to collect data over longer time period to provide greater precision in the data near the threshold sensitivity of the counter. Most benchmark data has been collected at Point of Delivery (POD) or Point of Entry (POE) and is the basis for parameters. This particle counting efficiency is not taken into account, which may vary with particle counter model, particle materials, chemical, etc.. It is based on actual data reported.
[12] SMC Organics: Single wafer shall be oxidized to make organic-free, then wafer shall be exposed for 24 hours and top side analyzed by TD-GC-MS with 400°C thermal desorption, and quantitation based on hexadecane external standard. TIC response factor per SEMI MF 1982-1103 (formerly ASTM 1982-99).[4] Limits determined by above method are a guideline for many organics. Note higher limits can be used for process wafers oxidized or cleaned prior to subsequent process step. Processes such as gate oxide formation, or polysilicon deposition, may be more sensitive to organics, especially high boilers such as DOP. Silicon nitride nucleation may also be more sensitive than above for some processes. Please note dopants requirement is covered in earlier section. Contamination levels are time based, and samples should be exposed for a weeks time for better sensitivity; ng/cm2/week. Total contamination level on reticles that cause problems also vary with energy exposure. These guidelines subject to change with new data currently being generated.
[13] SMC Dopants: Single wafer is first stripped with HF to yield dopant-free surface and than exposed for 24 hours. Topside of wafer is analyzed by methods known to give reliable recovery of boron. This is a guideline for dopants based on sampling in operating running fabs. Lower specifications may be required for key FEPs, especially for smaller geometries, lower thermal budgets, and for lightly-doped devices. If wafers are stripped with HF or BOE immediately prior to next thermal process, then steps may become less sensitive to surface molecular dopants, and higher limits apply. Note that BEPs tend to be orders of magnitude less sensitive to dopants than FEPs.
[15] SMC General: A 24-hour exposure will accentuate the contamination per wafer as wafers are often exposed too much shorter times in actual processing. The above SMC (surface molecular contamination) limits are preliminary, and no single value applies to all process steps or types of organics, dopants or metals. The SMC limits can vary substantially from process to process, and local air purification or purges may be needed to control contaminant levels.
[16] Dissolved oxygen (DO) has an effect on pre-gate oxide cleaning and the etch rate of non H-passivated SiO2 and copper structures. The level in the table is that of the most stringent. It is expected that slightly higher levels within the same order of magnitude would not have any significant effect on manufacturing processes. If the water for a specific processes need to remain at low oxygen concentrations lower levels of dissolved oxygen could provide somewhat larger process time windows before critical concentration levels are reached. It is known that some fabs consider DO a process variable and operate at DO levels 3 orders of magnitude higher than stated in the table. Corrosion rates as a function of DO are not a linear relationship for all materials, specifically copper etch rates are near a maximum at 300 ppb DO. DO spec is considered at POE, taking into account possibility that N2 blanketing may be provided at the tool level.
[17] Uncertain at this time what target levels might be set given the variety of chemistries used in the industry and unknown sensitivity of the wafer to particles or ionic contamination in the chemical. This parameter is identified as a potentially critical one that should be considered and work is ongoing to define the correct levels.
[18] The value of silica (now measured as reactive silica) used in the roadmap is at current low practical detection limit and it is supposed to indicate the overall health of the system. In 2018 revision, "Proactive" silica parameter was added to enable risk mitigation of colloidal silica occurrence by controlling silica in the feed to the Polish loop of UPW system. Silica may occur in UPW in a form of reactive (dissolved) or colloidal silica. Colloidal silica is considered detrimental for the semiconductor manufacturing. However, the killer particle size of currently considered generations became so small, making it impractical to expect that the colloidal silica might be measured as delta between total and reactive silica in UPW (the practice used in the past). Hence, colloidal silica is considered to be controlled as particles down to non-detectable (as silica) level. As the result only reactive silica is relevant in the silica requirement. For practical purposes testing for either total or reactive silica can be used. However, measuring both total and reactive silica may not be considered to confirm presence of colloidal silica. In high concentration (1 ppb), dissolved Silica is a potential cause for water spotting. When boron is controlled below or near limits of boron detection the level of dissolved silica is usually bellow the limits of detection as well. The silica specification is considered at POC (point of connection) based on the industry experience – no water marks were reported at the specified level. It is expected that the wafer will leach silica, adding silica level on the top of UPW level.
[19] The list of critical metals (e.g., Al, Ca, Cu, Fe, Mg, Ni, K, Si, Na) varies from process to process depending on the impact on electrical parameters such as gate oxide integrity or minority carrier lifetime as well as mobility of the metal in the substrate. The metals listed in note [G] for liquid process chemicals are of concern but the issues around metals in specialty gases are primarily around the potential for corrosion to add metal particles to the gas flow (e.g., Fe, Ni Co, P). The potential for volatile species containing metals must be considered for each specialty gas but are generally not present in the bulk gases. In 2018 revision, critical metals for image sensors manufacturing facilities have been added. Those metals were reported to cause defect in image sensors (see also note #39 below).
[20] The following is a complete list of metal ions of concern in certain liquid chemicals: Ag, Al, As, Au, Ba, Ca, Cd, Co, Cr, Cu, Fe, K, Li, Mg, Mn, Mo, Na, Ni, P, Pb, Pd, Pt, Ru, Sb, Sn, Sr, Ti, V, W, Zn.
[21] Elements listed that are not in parentheses may cause high or some risk to device quality and may often be present in process chemicals. Elements listed that are in parentheses may cause high risk to device quality but are not typically present in process chemicals.
[22] TOC on-line measurement remains the reference detection method for the presence of total organics in UPW. Users of this roadmap are encouraged to speciate organics in their UPW. For non-critical organics the limit is 3 ppb. For critical organics and immersion lithography where UPW comes in contact with the lens, the limit is 1 ppb. Less than 1 ppb of Total Organic Carbon was proven successful for immersion lithography operation and preventing lens hazing, Total Organic Carbon in UPW is defined as equivalent amount of CO2 produced from UV oxidation at 185 nm wavelength inside of the UV reactor of a TOC monitoring device. Currently used online, TOC analyzers are non-specific in their measurement of organic contaminants. Some organics are expected to have higher impact to the semiconductor manufacturing than others, hence TOC specification has been replaced with critical and non-critical organics for all applications, including immersion photolithography. Critical Organics are those with the highest boiling point. Organics with high boiling points could deposit on the wafer surface in a high temperature furnace and result in the formation of silicon carbide. This is considered a fatal defect at levels of 1.0E+12 atoms per cm2 as C. The boiling point of organic compounds is used to categorize them as a “critical”. At this time, any organic compound with a boiling point higher than 200°C is considered critical. Based on past experience acceptable concentration of total critical organic compounds is <1.0 ppb (as measured by on-line instrumentation). Non critical organics is proposed to be as high as 3.0 ppb. Modeling and experimental analysis are in progress to validate correlations of critical organic compounds to device defects. The end user may want to consider POU solutions for immersion litho if 1.0 ppb TOC water quality is chosen to be controlled for the immersion lithography tools, independently of the type of the organics comprising TOC. In addition to the boiling point characteristics, size of the organic molecule becomes another important consideration. Very high molecular weight dissolved organics may form particles on the wafer as the water dries out. This phenomenon was confirmed experimentally refer to supplemental information) and hence the particle related concern is growing as dimensions become smaller. At this point 500,000 Dalton and larger is considered to be the size of the organic molecule potentially forming killer size particles. The color in the YE3 table is provided to indicate the need of metrology development for online measurement of critical organics, as well additional work needed to better define the critical organics via FMEA. The organics specification is defined at the POE (Point of Entry) to the manufacturing tools, assuming that control of the organics level is provided outside of the tools, whereas the manufacturing process technology takes into account contribution by the tool materials and chemistry used.
[23] The photolithography AMC guidelines are for tools with ArF lasers only, and are based on inputs from the Litho TWG. The critical metrology guidelines are from the metrology TWG. All photolithography tools and some metrology equipment have chemical filters on the makeup air to the internals of the tools. These filters have a finite lifetime, which is dependent on the contaminant loading. Providing a chemically cleaner environment will extend the life of these filters.
[24] Other critical ions may include inorganic ions such as Fluoride, Chloride, Nitrate, Nitrite, and Bromide, Sulfate as well as ammonium. However no reference was currently found that these ions in typical concentrations found in ultrapure water up to 50 ppt have any impact on the process. Phosphate specification level was defined at 20 ppt based on higher risk of deposition. Also for organic anions such as acetate, formate, propionate, citrate, and oxalate no harmful levels have been established up to now. The ions specification is considered at POP (point of process) due to assumption that both UPW system as well as POU filters may be used to control metals, while tool environment may contribute metal contamination. Ammonium, sulfate, and nitrite can be contributed by air.
[25] The variety of CVD and ALD precursors is continuously increasing as well as their applications. The contaminant types and levels vary widely due to the different chemical behavior. An overview about typical precursors is therefore given in attachment Precursor table.
[26.1] The maximum allowed particle concentration in UPW has been updated based on the following assumptions and considerations: A. The maximum concentration of particles in UPW is a function of the allowed defect level on the wafer as defined in the More Moore table and particle deposition form UPW to the wafer surface. The reference point will be the critical particle size. The relationship between acceptable particle concentrations on the wafer and that in UPW is based on experimental data (see supplemental materials for reference) and theoretical modeling. The user of this part of the table is encouraged to refer to the supplemental materials for specific details of the calculations. B. The table now recognizes Electrical Active Particles (EAP) as a significant particle category. EUV has its own critical particle size, together with its own more strict particle detection limits. Significant metrology hurdles for particles at the critical size still exist. Given the fact that the metrology gap is growing and has not been addressed for last decade, the risk management for particle control is being shifted towards proactive effective mitigation measures, including particle filtration and reduction of the particle challenge to the final filters. The concept is to measure particle levels using existing particle and widely used metrology at 50 nanometer detection prior to the final filter. Using the desired particle concentration after the final filter and the particle power law, particles levels at 50 nanometers can be predicted, and monitored in UPW before the final filter. This approach is used when defining "proactive" particle control parameter. This idea is being incorporated with a SEMI task force produced guides ([5] SEMI C079) for filter performance validation, as a method to control the particles on the wafer surface and mitigate the risk of particle contamination impacting yield. A similar task force has developed a test method for evaluation of the cleanliness of the virgin ion exchange resin, SEMI C093. [6]. [26.2] Colloidal silica is now treated as a non-electrically active particle. However, as stated before, existing UPW metrology is not sensitive enough to allow the detection of colloidal silica particles at the specified size. So pro-active measures must be taken, such as described above, to mitigate the impact of any colloidal silica particles on the wafer. Silica particles are believed to have the ability to adsorb metals and act as a transport mechanism to potentially deposit metals on the surface of a wafer. Such metal deposition could seriously impact yield. [26.3] An additional particle requirement has been specified for EUV mask production, which also requires tight particle control. The target concentration is an order of magnitude lower than that specified for high volume manufacturing facilities (refer to supplemental information for additional details). The killer size of the particles for this application is a function of the EUV wavelength. [26.4] Supplemental information shows different mechanisms whereby a particle can effect device performance. A particle that bridges current flow is considered to be most critical. Such a particle may be even smaller than the currently define critical particle size. The particles specification is considered at POP (point of process) due to assumption that both UPW system, critical components, as well as tool environment may generate particles, taking into account capabilities of both UPW delivery system (including POU filters) and the tool environment contribution. However, for the practical purposes, the assumption​ is that most particles will be contributed by the tool, thus requiring even higher UPW quality targets at POE (point of entry).
[27] It needs to be considered that the total H2O2 anion concentration will impact the life time of the solution. Also the fluoride in the ppm range of the total chemical mixture can etch the wafer.
[28] Concentrations higher than 100 ppb could cause corrosion especially in back end of line processes.
[29] The ultrapure water parameters provided in this table are applicable for the most critical process unless otherwise identified by additional footnotes. Further information can be found in the Supplementary tables.
[30] Typical Organic Acids found in cleanroom environments that may be of concern include Acetate, Citrate, Formate, and Propionate. Others may also be of concern.
[31] Ideally, continuous monitoring using online instrumentation would be preferred when practical since this can give both long term averages and catch excursions. When online monitoring is not available, an average grab sample for at least 4 hours, and not more than 24 hours is recommended, to get an average, increase sensitivity of the analysis, and avoid short term transient effects.
[32] Other corrosive species include contaminants such as chlorine. Humidity is also of major concern, as it exacerbates corrosion. The humidity should be kept as low as possible in corrosive environments.
[33] Calculations for expressing ng/L into ppt are; [(ng/(L of Air) * (24.4 L of Air)/mol Air / MW(ng/nmol)) * *1000picomol/nmol ] = picomol/mol of Air = ppt molar and/or ppt volume.
[34] For certain processes such as sputtering POE purifiers may be required for N2 and Ar
[35] CO2 here is assumed to be used for wet cleaning and other equipment, not for super critical CO2 applications or dry etching.
[36] Epi – need to purify @ 45 nm; currently must add purifiers from B2H6/Germane/PH3/AsH3 – need 100 ppb
[37] The variation is defined at one location over time in at rest conditions. As reference point for the POE a location is chosen 0.3 m below the ceiling panels. Common sense requires that sensitive equipment are not installed heat sources within the cleanroom, since they may impact the temperature control between the reference point and the actual inlet to the mini-environment/tool filter.
[38] This temperature stability requirement is for immersion photolithography tools, using UPW as an immersion fluid, and based upon utility requirements projected by some tool manufacturers in 2005. It represents the maximum rate of change and stability of the temperature of the cold UPW supplied to the tool in order for the tool to maintain process required temperature stability.
[39] The list of metals was increased to 24 elements to include additional elements listed in 2013 FEP table. Values based on FEP definitions of criticality to process. Users of the Table are strongly encouraged to review the Metal White Paper in supplemental materials for additional information. Metals such as Mo, W, Ti, Au*, Pt*, Cu, Mn, Ag*, Co are considered to be particularly important for CMOS sensors – special parameter was added to the roadmap. Metals with asterisk next to them are only recommended to be controlled if their occurrence is expected and sources are know. Those metals (Au, Pt, and Ag) are particularly difficult to measure at very low levels and they typically do not occur unless use in the facility or reclaimed together with used water from the manufacturing process. The metal specification is considered at POP (point of process) due to assumption that both UPW system as well as POU filters may be used to control metals, while tool environment may contribute metal contamination. In 2018 revision, additional "proactive" parameter for the metals control was added for the feed to the Polish system (UPW tank). This is due to the fact that many of those metals cannot me measured at the target level but have to be controlled.
[41] The resin by-products are only a small part of the organics in H2O2, but have shown the most serious effects on the wafer. The organics leached out from the resins are different depending on the type of resin, but have shown a much higher sticking potential than the other solvents in the H2O2. Total amines are mentioned here as an example only. Measurement of these organics is possible, e.g. by ion chromatography or liquid chromatography with mass spectrometer, but there a variety of problems, such as the sample preparation since these compounds can be very volatile/sensitive.
[42] Hydrogen peroxide (H2O2) was confirmed to be produced by UV (ultraviolet) lamps in the polish loop at the levels of up to 30 ppb, the level exceeding dissolved oxygen, which is also considered to be an oxidant. The effect of specific level of H2O2 to the wafer has not been fully validated yet. Experimental work conducted by Screen (see supplemental information) indicated that 10 ppb of H2O2 resulted in impact to the surface properties of copper compared to that of 1 ppb UPW. For the practical purposes 3 ppb H2O2 was defined as target for the roadmap. At this level of H2O2 it is expected that improvement in the process performance will be enabled, while no substantial capital investment, which likely is required for the lower level. H2O2 control is considered at POD (point of distribution) based on the assumption that no H2O2 production is expected downstream that point.
[44] There is an opinion that the limit value of 0.5 ppbv total inorganic acids is too strict; Experience exists that 2 ppbv would be an acceptable limit value maintaining good yield/no or low defect conditions
[45] Particles for static critical components is in #/l in UPW (tubing and non actuated components) It is per actuation for actuated components. These values are from the More Moore defect density calculator. The particle contribution from actuated components can be converted to concentration/liter by using the model and testing done for SEMI F104.
[46] Critical components includes all high purity components in the flow stream for liquid delivery and is focused on the last filter and beyond (i.e., close to wafer). This includes pipe, tube, valves, control elements, filters that are integral to final delivery.
[48] Effect of any contaminants from critical components on wafer is not yet understood.
SEMI MF1982-1103 (previously ASTMF 1982-99e1), Standard Test Methods for Analyzing Organic Contaminants on Silicon Wafer Surfaces by Thermal Desorption Gas Chromatography, SEMI.
SEMI C79-0113 GUIDE TO EVALUATE THE EFFICACY OF SUB-15 nm FILTERS USED IN ULTRAPURE WATER (UPW) DISTRIBUTION SYSTEMS. Www.semi.org
SEMI C093: GUIDE FOR DETERMINING THE QUALITY OF ION EXCHANGE RESIN USED IN POLISH APPLICATIONS OF ULTRAPURE WATER SYSTEM
[49] Chemistry containing Micelles will require a larger particle size threshold to be used to prevent counting Micelles as harmful particles.
[51]SEMI F57 experimental testing to measure extraction rates for critical components used in UPW was completed and the data used in models for UPW and HUPW to confirm the values in the table. The test was to confirm rinse up of new material in 30 days.
[52] Filters used in the POP ("final filters") location should be designed to minimize particle shedding from those filters. This requires consideration of filter design, material of construction and fluid system design and operation. Use of SEMI C79-0819 is recommended for the filter selection and qualification.
[54]Critical components quality should support ambient UPW requirements through 2023. For HUPW more critical evaluation of materials should be considered to meet requirements. Current generation of HP materials should suffice for both critical and non-critical organics
[55]If a critical component will work for UPW then it should also work for UHP chemicals except for possible acid extraction of metals.
[56] The critical particle size for the manufacture of semiconductors is now below 5 nm. The semiconductor industry is entering a region where particles, particle precursors and molecules in liquids, begin to overlap. A particle precursor is defined as a dissolved molecular compound, which may form particles on the wafer. The ability to distinguish particle precursors from solid particles in UPW is becoming critical. While advanced filtration can remove nanometer sized solid particles, the same filter may have little or no ability to remove particle precursors. The use of combination of Nebulization and Condensation Particle Counting (N+CPC) measurement techniques have shown promise in detecting these particle precursors. This measurement techniques use aerosol particle detection, reconfigured to measure particles in liquids. NIST has extensively used the Nebulization and Particle Counting after Electrical Mobility Size Classification method of measuring particle size. The precursors are measured in the units of the number of particles produced in N+CPC instrument per milliliter of UPW. It is important to note that the particle precursor parameter cannot be detected with use of currently available metrology at that level defined in the roadmap and therefore should not be used as specification for any purpose other than a target for future technology development around metrology, material purity, and treatment technology. The available metrology does not have a standard to verify the quality of the data produced. The quality of the results relies on the source specific calibration/verification methods.
[57] HMW organics in IPA was determined to be any organic with a boiling point higher than that of IPA (82.5 C) and any organic with > 14 Carbon atoms. These larger organics have been seen to cause defects on the wafer
[58] Particles from POU filters are NOT covered by this document. It is important to note that any filter that operates in an on/off mode will likely shed particles.
[59] The specification for dynamic components is specifically for final dispense valves post POU filter, (or any dynamic component post POU filter) POP. Dynamic components upstream of filtration will have benefit of filtration removing particles.
[60] There is some evidence that shows that the Powers law may not be valid for filtration of small particles.
[61] NVR (non volatile residue) refers to residues left on the wafer surface during the wafer process. It can be anything that remains. These are known yield impactors and may . For Critical Components it is likely to be organics, metals or fluorine from materials of construction. There can also be particles from polymer surfaces that have aged and stress brittled or have suffered oxidation and broken polymer chains. Further work needs to be done to identify and categorize these contaminants.
[62] Critical Organics - As defined by the UPW roadmap a critical organic is a particle precursor. Per that definition (note [22]) they do not apply to Critical Components. For critical components we will use the organic as defined in NVR in note [60]. Organics that have properties similar to cyclo-hexanone or cyclo-hexanol would be more appropriate as an organic species of interest in both molecular weight and boiling point (150oC). Larger molecular weight and higher boiling point materials would also be a problem.
[63] Critical Components to get at least 50% due to shipping, storage, chem delivery and dispense surfaces. This is especially true for new vs reused containers. New containers and components tend to have more extractables (organics and/or metals) and the old components/containers tends to shed more particles. This is specific for HP polymers. Any Stainless Steel used in IPA should at least be 316L, CFOS.
[64] There are currently three definitions of Critical Organics: UPW, UHP Chems and CC. This needs to be reviewed to see if each require a unique definition. The testing for defining what a critical organic is for Critical Components will occur in 2022.

## Table YE3a
INDEX
Table 3a Limit values for interfering atoms on surfaces; avoidance of critical defect densities, various process stages (from the chapter More Moore)
| Contaminants | Type | Module | Process Step | Mechanism | Defect Density as measured | Model substance | Comments & potential failure mechanism
| Carbon | atomic carbon, post thermal treatment | Source drain & gate stack | Dry etch | Surface damage blocking the dopant (B,P) diffusion in the extension region | 5 e13 at/cm2 | DEP, DBP, DOP, Ethyl-propionate | Can occur on air break after cleaning. Deterioration of device performance is explained by means of positively ionized carbons at the interface actin as additional positive charges affecting the inversion to n-channel
| Organics | Molecular | Gate stack | Standard clean | Carbon compounds induces the expansion of the silicon oxide lattice, deteriorating the silicon oxide layer, resulting in the device failure | 5 e11 at/cm2 | DEP, DBP, DOP, Ethyl-propionate | Sources of organic contamination are chemical surface modification (i.e. hexamethyldisilazane priming), wafer box storage and extended vacuum exposure. Major organic molecules in the cleanroom air are volatiles outgassing from polymeric materials. They are affecting subsequent CVD steps controlling the film thickness.
| Oxidizers | H2O2, O2, O3 | SD/MOL, metal | Air break thermal anneal | Si and/or metal oxidation | 1 e10 at/cm2 | ozone | Oxygen and moisture in the ambient air. Si-O-Si, Si-H and Si-OH species; very dilute solutions of HF, in de-ionized water, DI, or dilute solutions of ammonium fluoride, NH4F, HF and DI water (buffered oxide etch, BOE) completely remove silicon native oxide, leaving a hydrogen-terminated clean silicon surface a

## Table YE3b
INDEX
Table 3b Model results critical times (tcrit) to reach the limit values for impurity atoms for different process stages; model substances
| Model substance | Defect density limit | Impact concentration c0 | Critical time tcrit
| DEP (Diethyl phtalate) | 5e11 at C/cm2 | 1000 pptv | 22 sec
|  |  | 100 pptv | 228 sec
|  |  | 10 pptv | ¥
|  | 5e13 at C/cm2 | 1000 pptv | ¥
|  |  | 100 pptv | ¥
|  |  | 10 pptv | ¥
| DOP (Dioctyl phtalate) | 5e11 at C/cm2 | 1000 pptv | 14 sec
|  |  | 100 pptv | 143 sec
|  |  | << 1 pptv | ¥
|  | 5e13 at C/cm2 | 1000 pptv | 1’430
|  |  | 100 pptv | 15’500
|  |  | 18 pptv | ¥

## Table YE4
INDEX
Table YE 4 AMC Monitoring Methods
| Year of Production | 2022
Flash ½ Pitch (nm) (un-contacted Poly)(f)
DRAM ½ Pitch (nm) (contacted)
| MPU/ASIC Metal 1 (M1) ½ Pitch (nm) | 12
MPU Printed Gate Length (nm) ††
MPU Physical Gate Length (nm)
Wafer Environment Control such as Cleanroom, SMIF POD, FOUP, etc….not necessarily the cleanroom itself but wafer environment.
| Critical particle size (nm) [1] | 9
| Number of particles (/m3) [1,2] | ISO CL1 | Measurement methods
| Airborne Molecular Contaminants in Gas Phase (pptV, V for Volume)) [3,7,12,13,14,15,33]. |  | Online Monitoring |  | Wet or Dry Impinger Sampling [7] |  |  |  |  | Passive/Diffusive Sampling (Beaker/Dry trap) [11] |  |  |  | TD GC-MS |  |  |  |  | Surface analysis
|  | Limits from YE3 table | Method | LDL (pptV) | Method | LDL (pptV) | Sample volume (L) | Sample flow rate (LPM) | Sample frequency | Method | LDL (pptV) | Sample duration (d) | Sample frequency | Method challenges | LDL (pptV) | Sample volume (L) | Sample flow rate (LPM) | Sample frequency | Method | LDL (pptV)
Gate stack (Gate oxide and gate oxide pre-clean), POE (Point of Entry)
| Total Inorganic Acids (HF, HCl, HBr, HNO3, H3PO4, H2SO4, excluded HNO2); POE | 2'000 (total); 500 (individual) | CRDS [1] *) | 30-350 | IC-Conductivity [8,9] | 10-100 | 1500-200 | 2022-01-05 | Every 2 months | IC-Conductivity [8,9,12] | 100 | 7-90 | Every 3 month
|  |  | IMS [2] | 200 [13] 70 [14]
|  |  | UV-F [3] *) | 500
| Total Organic and Inorganic Bases; POE | 1000 | PTR-MS [4] *) | 10-500 | IC-Conductivity [8,9,10] | 10-100 | 1500-200 | 2022-01-05 | Every 2 months | IC-Conductivity [8,9,10,12] | 100 | 7-90 | Every 3 month | For organic amines only (not total bases) Cut at C28 | 100 | 20-40 | 50-200 | Every 2 months
|  |  | IMS [2] | 200
|  |  | CRDS [1] *) | 200-300
|  |  | CLD [5] | 500
| Total Organics > C6 , (aliphatics, conjugated, ketones, aldehydes, esters and others w/ GCMS retention times ≥ benzene, calibrated to hexadecane) [31]; POE | 1000 | PTR-MS [4] *) | 10-200 | [5 empty] | TD, GC-MS | 100 | 7-90 | Every 3 month | Cut at C28 | 100 | 20-40 | 50-200 | t.b.d
| Total Organic Compounds and Inorganic compounds that contain P, B, As (Dopants); POE | 100 | PTR-MS [4] *) | 100-200 | [9 empty] | Use special GC column | 100 | 20-40 | 50-200 | t.b.d
Source Drain Contact module (Trench Etch & EPI) POE
| Total Inorganic Acids (HF, HCl, HBr, HNO3, H3PO4, H2SO4, H2SO3, SO2, excluded HNO2), each; POE | 10 (individual) | CRDS [1] *) | 30-350 | IC-Conductivity [8,9] | 100 | 200-500 | 2022-01-05 | Every 6 months | IC-Conductivity [8,9] | 100 | 7-90 | Every 3 month
|  |  | IMS [2] | 200 [13] 70 [14]
|  |  | UV-F [3] *) | 500
| Total Organic and Inorganic Bases; POE | 100 | PTR-MS [4] *) | 10-500 | IC-Conductivity [8,9,10] | 100 | 200-500 | 2022-01-05 | Every 6 months | IC-Conductivity [8,9,10] | 100 | 7-90 | Every 3 month | Use special GC column | 100 | 20-40 | 50-200 | Every 6 month
|  |  | IMS [2] | 200 [13] 70 [14]
|  |  | CRDS [1] *) | 200-300
|  |  | CLD [5] | 500
| Total Organic Acids [30]; POE | 100 | PTR-MS [4] *) | 50-200 | IC-Conductivity [8,9] | 100 | 200-500 | 2022-01-05 | Every 6 months | IC-Conductivity [8,9] | 100 | 7-90 | Every 3 month
| Total Organics > C6 , (aliphatics, conjugated, ketones, aldehydes, esters and others w/ GCMS retention times ≥ benzene, calibrated to hexadecane) [31]; POE | 100 | PTR-MS [4] *) | 10-200 | [9 empty] | Cut at C28 | 100 | 20-40 | 50-200 | t.b.d
Via Formation (Via bottom clean & post-CMP clean) & Metallization, POE (Point of Entry)
| Total Inorganic Acids (HF, HCl, HBr, HNO3, H3PO4, H2SO4, H2SO3, SO2, excluded HNO2); POE | 200 | CRDS [1] *) | 30-350 | IC-Conductivity [8,9] | 100 | 200-500 | 2022-01-05 | Every 6 months | IC-Conductivity [8,9] | 100 | 7-90 | Every 3 month
|  |  | IMS [2] | 200 [13] 70 [14]
|  |  | UV-F [3] *) | 500
| Total Organic Acids [30]; POE | 500 | PTR-MS [4] *) | 50-200 | IC-Conductivity [8,9] | 100 | 200-500 | 2022-01-05 | Every 6 months | IC-Conductivity [8,9] | 100 | 7-90 | Every 3 month | Use special GC column | 100 | 20-40 | 50-200 | Every 6 month
| Total Organics > C6 , (aliphatics, conjugated, ketones, aldehydes, esters and others w/ GCMS retention times ≥ benzene, calibrated to hexadecane) [31]; POE | 1000 | PTR-MS [4] *) | 10-200 | [5 empty] | TD, GC-MS | 100/- ??? | 7-90 | Every 3 month
| Reactive Sulphur compounds (e.g. H2S) | 500 | PTR-MS [4] *) | 100
|  |  | IMS [2] | 200 [13] 70 [14]
|  |  | UV-F [3] *) | 500-600
| Oxidizers (e.g. Ozone) | 5000 | UV-A [6] *) | 600
Methods and instruments are known and are being optimized
Methods and instruments are known and in preparation for production
| ¿ | Methods and instruments are in beta tool status under qualification
Detection Limit of the Instrument is in the range or higher as the defined Limit concentration; may concern only specific components; for details refer to the methods overview table (YE 4a)
| Edition 2022, Table YE4: | Table YE4 has been updated to match table YE3 with reference to it's structure and content. The monitoring technologies have been evaluated on the basis of their technical capabilities in the year of evaluation 2021.
Footnotes from first column : Please refer to YE3 table footnotes.
Footnotes
[1] CRDS Cavity Ring Down Spectroscopy; for method key features and capabilities please refer to the methods overview table (YE 4a)
[2] IMS Ion Mobility Spectrometry; for method key features and capabilities please refer to the methods overview table (YE 4a)
[3] UV-F UV Fluorescence; for method key features and capabilities please refer to the methods overview table (YE 4a)
[4] PTR-MS Proton Transfer Mass Spectrometry; for method key features and capabilities please refer to the methods overview table (YE 4a)
[5] CLD Chemiluminescence Detection of NO y compounds, for method key features and capabilities please refer to the methods overview table (YE 4a)
[6] UV-A UV Absorption; for method key features and capabilities please refer to the methods overview table (YE 4a)
[7] Impinger sampling for FOUP and other micro-environments is only applicable for continuous purge outgas testing, not for static volume testing, due to the limited volume of the device.
[8] Ion Chromatography Mass Spectrometry (IC/MS) may be used to identify unknown species
[9] Capillary electrophoresis mass spectrometry (CE/MS) may be used with probable higher detection limits
[10] Liquid chromatography mass spectrometry (LC/MS) may be used for organic bases
[11] Due to its long sampling time, passive sampling (formerly beaker sampling) is recommended only for long-term averaging of AMC concentrations.
[12] Open beakers are not suitable for compressed gas analysis. Dry passive samplers would work.
[13] IMS instrument as part of an additional multipoint sampling systems, external effects by tube materials etc. have an impact on LDL and systems performance
[14] single IMS instrument only (w/o any additional sampling systems)
*) Method is capable to detect and quantity individual compounds. Sum values are therefore the results of summing up individual concentrations

## Notes for Table YE4
INDEX | Notes for Table YE4 AMC Monitoring
Footnotes from first column : Please refer to YE3 table footnotes.
Footnotes
[1] CRDS Cavity Ring Down Spectroscopy; for method key features and capabilities please refer to the methods overview table (YE 4a)
[2] IMS Ion Mobility Spectrometry; for method key features and capabilities please refer to the methods overview table (YE 4a)
[3] UV-F UV Fluorescence; for method key features and capabilities please refer to the methods overview table (YE 4a)
[4] PTR-MS Proton Transfer Mass Spectrometry; for method key features and capabilities please refer to the methods overview table (YE 4a)
[5] CLD Chemiluminescence Detection of NO y compounds, for method key features and capabilities please refer to the methods overview table (YE 4a)
[6] UV-A UV Absorption; for method key features and capabilities please refer to the methods overview table (YE 4a)
[7] Impinger sampling for FOUP and other micro-environments is only applicable for continuous purge outgas testing, not for static volume testing, due to the limited volume of the device.
[8] Ion Chromatography Mass Spectrometry (IC/MS) may be used to identify unknown species
[9] Capillary electrophoresis mass spectrometry (CE/MS) may be used with probable higher detection limits
[10] Liquid chromatography mass spectrometry (LC/MS) may be used for organic bases
[11] Due to its long sampling time, passive sampling (formerly beaker sampling) is recommended only for long-term averaging of AMC concentrations.
[12] Open beakers are not suitable for compressed gas analysis. Dry passive samplers would work.
[13] IMS instrument as part of an additional multipoint sampling systems, external effects by tube materials etc. have an impact on LDL and systems performance
[14] single IMS instrument only (w/o any additional sampling systems)
*) Method is capable to detect and quantity individual compounds. Sum values are therefore the results of summing up individual concentrations

## Table YE4a
INDEX
Table YE 4a Supporting Table for On-line Methods
| Class and type of Molecular Contamination |  | LDL / Limit of quantification | Measurement Range | Matrix | Data interval | Sample flow** | response time t95 | recovery time t05 | zero point*** | span drift**** | interference | service interval | multipoint | measurement | information | source | source | source | literature reference
| (to SEMI F 21-1102, ITRS Definitions of AMC and CAS-N°) | CAS-N° | (pptv) | (pptv) * | (air, others) | (sec) | (ml/min) | rise (sec) | decline (sec) | drift (%/month) | (%/month) | to (% of signal) | (months) | sampling capability***** | principle | year of entry | supplier | IDM | IRDS team | ( publication with IDM/academia)
MA (Molecular Contamination of Acid or acid precursor type)
| Total Inorganic Acids as sum value****** | n.a. | 200 (with Multipoint unit) 70 (instrument only) | 0 - 5E+4 | air | 30 | 600 | < 300 120 (t90) | < 300 | 2% (autozero) | 2 | 5% of NOx | 6 months | up to 64 ports | Ion Mobility Spectrometry (IMS) | 2018 |  |  | ●
| HF (Hydrogen Fluoride) as individual compound | 7664-39-3 | 30 - 75 | 0 - 1E+6 | air | 4 | 2000 | 120 | 60 | +/- 150 pptv | +/- 5% full scale |  | 12 months | up to 16 ports | Cavity Ring-Down Spectroscopy (CRDS) | 2021 | ● |  | ●
| HCl (Hydrogen Chloride) as individual compound | 7647-01-0 | 45 - 100 | 0 - 2E+6 | air | 3 | 2000 | 120 | 60 | +/- 30 pptv | +/- 5% full scale |  | 12 months | Yes | Cavity Ring-Down Spectroscopy (CRDS) | 2021 | ● |  | ●
|  | 7647-01-0 |  | 0 - 5E+4 | air | 30 | 250 | < 300 | < 300 | 2% (autozero) | 2 | 5% of NOx | 6 months | up to 64 ports | Ion Mobility Spectrometry (IMS) | 2018 |  |  | ●
| NOx (representing NO+NO2) | n.a. | 300 | 0 - 1E+6 | air | 20 | 500 | 10 | 20 | <+/- 200 pptv | <1% | CO2 | 12 months |  | Chemiluminescence CLD | 2021 |  |  | ●
| SO2 (Sulfur Dioxide) as individual compound | 2025884 | 350 | 0 - 1E+6 | air | 5 | 200 | 15 | 15 | +/- 300 pptv | +/- 5% full scale |  | 12 months |  | Cavity Ring-Down Spectroscopy (CRDS) | 2021 | ● |  | ●
|  | 2025884 | 200 | 0 - 5E+4 | air | 30 | 250 | < 300 | < 300 | 2% (autozero) | 2 | 5% of NOx | 6 months | up to 64 ports | Ion Mobility Spectrometry (IMS) | 2018 |  |  | ●
|  | 2025884 | 500 | 0 - 5E+5 | air | 10 | 500 | 120 (t85) | 60 | < +/- 200 pptv | <1% | 2% of NOx, HC | 12 months |  | UV Fluorescence (UVF) | 2021 |  |  | ●
| HFc (Formic Acid) as individual compound | 64-18-6 | 200 | 0 - 1E+6 | air & nitrogen | 180 | 50-500 | 5 | 10 | 0% (weekly zero) |  |  | 3-6 months | up to 64 ports | Proton Transfer TOF-MS (PTR-MS) | 2021 | ●
| HAc (Acetic Acid) as individual compound | 64-19-7
|  | 64-19-7 | 50 | 0 - 1E+6 | air & nitrogen | 30 | 50-500 | 5 | 10 | 0% (weekly zero) |  |  | 3-6 months | up to 64 ports | Proton Transfer TOF-MS (PTR-MS) | 2021 | ●
| HPr (Propionic Acid) as individual compound | 79-09-4 | 50 | 0 - 1E+6 | air & nitrogen | 180 | 50-500 | 5 | 10 | 0% (weekly zero) |  |  | 3-6 months | up to 64 ports | Proton Transfer TOF-MS (PTR-MS) | 2021 | ●
| HLac (Lactic Acid) as individual compound | 50-21-5 | 200 | 0 - 1E+6 | air & nitrogen | 180 | 50-500 | 30 | 10 | 0% (weekly zero) |  |  | 3-6 months | up to 64 ports | Proton Transfer TOF-MS (PTR-MS) | 2021 | ●
| Hox (Oxalic Acid) as individual compound | 144-62-7 | 200 | 0 - 1E+6 | air & nitrogen | 180 | 50-500 | 60 | 120 | 0% (weekly zero) |  |  | 3-6 months | up to 64 ports | Proton Transfer TOF-MS (PTR-MS) | 2021 | ●
MB (Molecular Contamination of alkaline nature, bases)
| Total Base as sum value****** |  | 200 (with Multipoint unit) 70 (instrument only) | 0 - 5E+4 | air | 30 | 500 | < 300 120 (t80) | < 300 | 2% (autozero) | 2 |  | 6 months | up to 64 ports | Ion Mobility Spectrometry (IMS) | 2018 |  |  | ●
| NH3 (Ammonia) as individual compound | 7664-41-7 | 500 | 0 - 1E+6 | air & nitrogen | 180 | 50-500 | 10 | 20 | 0% (weekly zero) |  |  | 3-6 months | up to 64 ports | Proton Transfer TOF-MS (PTR-MS) | 2021 | ●
|  | 7664-41-7 | 200-300 | 2 - 4E+6 | air | 5 | 2000 | 120 | 60 | +/- 150 pptv | +/- 5% at full scale |  | 12 months |  | Cavity Ring-Down Spectroscopy (CRDS) | 2021 | ● |  | ●
|  | 7664-41-7 | 500 | 0 - 1E+6 | air | 120 | 700 | 300 | 600 | <+/- 200 pptv | <1% | NOx | 12 months |  | Chemiluminescence CLD | 2021 |  |  | ●
|  | 7664-41-7 | 200 | 0 - 5E+4 | air |  | 500 | < 300 120 (t80) | < 300 | 2% (autozero) | 2 |  | 6 months |  | Ion Mobility Spectrometry (IMS) | 2018 |  |  | ●
| TMAH (Trimethylammonium hydroxide) as individual compound | 75-59-2 | 50 | 0 - 1E+6 | air & nitrogen | 30 | 50-500 | 10 | 20 | 0% (weekly zero) |  |  | 3-6 months | up to 64 ports | Proton Transfer TOF-MS (PTR-MS) | 2021 | ●
| Me3N (Trimethylamine) as individual compound | 75-50-3 | 200 | 0 - 1E+6 | air & nitrogen | 30 | 50-500 | 10 | 20 | 0% (weekly zero) |  |  | 3-6 months | up to 64 ports | Proton Transfer TOF-MS (PTR-MS) | 2021 | ●
Other amines as individual compounds, MEA, N-MEA
| NMP (N-Methylpyrolidone) as individual compound | 872-50-4 | 10 | 0 - 1E+6 | air & nitrogen | 30 | 50-500 | 20 | 40 | 0% (weekly zero) |  |  | 3-6 months | up to 64 ports | Proton Transfer TOF-MS (PTR-MS) | 2021 | ●
|  | 872-50-4 |  | 0 - 5E+5 | air | 30 | 250 | < 1 | < 180 | 0% (autozero) | 0.05 |  | 3-6 months | up to 64 ports | Ion Mobility Spectrometry (IMS)
| Total reduced Nitrogen, total amine****** | n.a. | 500 | 0 - 1E+6 | air | 120 | 700 | 300 | 600 | <+/- 200 pptv | <1% |  | 12 months |  | Chemiluminescence CLD | 2021 |  |  | ●
Other airborne compounds or alkaline nature
Molecular Contamination with Corrosive effects
| Total Corrosive Species as sum value****** | n.a.
| Cl2 (Chlorine) as individual value | 7782-50-5 | 200 | 0 - 1E+4 | air | 30 | 250 | < 1 | < 20 | 0% (autozero) | 0.05 |  | 3-6 months | up to 64 ports | Ion Mobility Spectrometry (IMS) | 2013
| Ozone | 10028-15-6 | 600 | 0 - 3E+5 | air | 10 | 700 | 30 | 30 | < +/- 500 pptv | <0,3% |  | 12 months | yes | UV Absorption (UV-A) | 2021 |  |  | ●
other corrosive species as individual value
MC (Molecular Contamination of Condensable Nature, Organics)
| Condensable Organics to SEMI F-21-95 (bp > 150 °C), sum value****** | n.a. | 200 | 0 - 1E+6 | air & nitrogen | 30 | 50-500 | 20 | 20 | 0% (weekly zero) |  |  | 3-6 months | up to 64 ports | Proton Transfer TOF-MS (PTR-MS) | 2021 | ●
| Volatile Organic Compounds (VOC) retention time > benzene | n.a. | 1950-05-01 | 0 - 1E+6 | air & nitrogen | 30 | 50-500 | 5 | 30 | 0% (weekly zero) |  |  | 3-6 months | up to 64 ports | Proton Transfer TOF-MS (PTR-MS) | 2021 | ●
| PGMEA (Methoxy-propyl-acetate) as individual compound | 108-65-6 | 50 | 0 - 1E+6 | air & nitrogen | 180 | 50-500 | 20 | 40 | 0% (weekly zero) |  |  | 3-6 months | up to 64 ports | Proton Transfer TOF-MS (PTR-MS) | 2021 | ●
| EL (Ethyl lactate) as individual compound | 97-64-3 | 20 | 0 - 1E+6 | air & nitrogen | 180 | 50-500 | 20 | 40 | 0% (weekly zero) |  |  | 3-6 months | up to 64 ports | Proton Transfer TOF-MS (PTR-MS) | 2021 | ●
| Other organic compounds (as individual compounds) |  | 5-500 | 0 - 1E+6 | air & nitrogen | 180 | 50-500 | 5 | 10 | 0% (weekly zero) |  |  | 3-6 months | up to 64 ports | Proton Transfer TOF-MS (PTR-MS) | 2021 | ●
Molecular Contamination of refractive type
Total Refractory compounds (containing Si, P, S) as sum value******
| HMDS (Hexamethyl-di-silazane) as individual compound | 999-97-4 | 50 | 0 - 1E+6 | air & nitrogen | 180 | 50-500 | 5 | 10 | 0% (weekly zero) |  |  | 3-6 months | up to 64 ports | Proton Transfer TOF-MS (PTR-MS) | 2021 | ●
| TMS (Trimethyl-silanol) as individual compound | 1066-40-6 | 50 | 0 - 1E+6 | air & nitrogen | 180 | 50-500 | 5 | 10 | 0% (weekly zero) |  |  | 3-6 months | up to 64 ports | Proton Transfer TOF-MS (PTR-MS) | 2021 | ●
| HMDSO (Hexa-methyl-di-siloxane) as individual compound | 107-46-0 | 30 | 0 - 1E+6 | air & nitrogen | 180 | 50-500 | 5 | 10 | 0% (weekly zero) |  |  | 3-6 months | up to 64 ports | Proton Transfer TOF-MS (PTR-MS) | 2021 | ●
| other linear siloxane compounds (as individual compounds) | n.a. | 10 | 0 - 1E+6 | air & nitrogen | 180 | 50-500 | 5 | 10 | 0% (weekly zero) |  |  | 3-6 months | up to 64 ports | Proton Transfer TOF-MS (PTR-MS) | 2021 | ●
| other cyclic siloxane compounds (as individual compounds) | n.a. | 10 | 0 - 1E+6 | air & nitrogen | 180 | 50-500 | 5 | 10 | 0% (weekly zero) |  |  | 3-6 months | up to 64 ports | Proton Transfer TOF-MS (PTR-MS) | 2021 | ●
| organo-phosphorous compounds (as individual compounds) | n.a. | 20 | 0 - 1E+6 | air & nitrogen | 180 | 50-500 | 20 | 40 | 0% (weekly zero) |  |  | 3-6 months | up to 64 ports | Proton Transfer TOF-MS (PTR-MS) | 2021 | ●
| organo-sulfur compounds (as individual compounds) | n.a.
MD (Molecular Contamination of Dopant type)
| Phosphorous compounds (airborne, of inorganic nature), PH3 | 7802-51-2 | 200 | 0 - 1E+6 | air & nitrogen | 180 | 50-500 | 5 | 10 | 0% (weekly zero) |  |  | 3-6 months | up to 64 ports | Proton Transfer TOF-MS (PTR-MS) | 2021 | ●
Phosphorous compounds (airborne, of organic nature)
| Arsenic compounds (airborne, or inorganic nature), AsH3 | 7784-42-1 | 100 | 0 - 1E+6 | air & nitrogen | 180 | 50-500 | 5 | 10 | 0% (weekly zero) |  |  | 3-6 months | up to 64 ports | Proton Transfer TOF-MS (PTR-MS) | 2021 | ●
Arsenic compounds (airborne, or organic nature)
Other dopant compounds (as individual compound)
Molecular Contamination of Sulfurous Nature
Total Sulfurous Compounds as sum value******
| H2S (hydrogen sulfide) as individual compound | 2148878 | 600 | 0 - 5E+5 | air | 60 | 500 | 60 | 120 | < +/- 200 pptv | <1% | 2% of NOx | 12 months |  | UV Fluorescence/Conversion (UV-F) | 2021 |  |  | ●
|  | 2148878 | 350 | 0 - 1E+6 | air | 5 | 200 | 15 | 15 | +/- 300 pptv | +/- 4ppb max or near LDL |  | 12 months |  | Cavity Ring-Down Spectroscopy (CRDS) | 2021
|  | 2148878 | 300 | 0 - 1E+6 | air & nitrogen | 180 | 50-500 | 5 | 10 | 0% (weekly zero) |  |  | 3-6 months | up to 64 ports | Proton Transfer TOF-MS (PTR-MS) | 2021 | ●
| SO2 (Sulfur Dioxide) as individual compound | 2025884 | 40 | 0 - 1E+6 | air | 5 | 1 000 - 2000 | 30 | 30 | +/- 300 pptv | +/- 4ppb max or near LDL |  | 12 months |  | Cavity Ring-Down Spectroscopy (CRDS) | 2021 | ● |  | ●
|  | 2025884 | 200 | 0 - 5E+4 | air | 30 | 250 | < 1 | < 20 | 0% (autozero) | 0.05 | 5% of NOx | 3-6 months | up to 64 ports | Ion Mobility Spectrometry (IMS)
|  | 2025884 | 500 | 0 - 5E+5 | air | 10 | 500 | 120 (t85) | 60 | < +/- 200 pptv | <1% | 2% of NOx | 12 months |  | UV Fluorescence (UV-F) | 2021 |  |  | ●
| Mercaptanes as individual compounds | n.a. | 100 | 0 - 1E+6 | air & nitrogen | 180 | 50-500 | 5 | 10 | 0% (weekly zero) |  |  | 3-6 months | up to 64 ports | Proton Transfer TOF-MS (PTR-MS) | 2021 | ●
| DMS (Dimethyl-sulfide) as individual compound | 75-18-3 | 100 | 0 - 1E+6 | air & nitrogen | 180 | 50-500 | 5 | 10 | 0% (weekly zero) |  |  | 3-6 months | up to 64 ports | Proton Transfer TOF-MS (PTR-MS) | 2021 | ●
|  | 75-18-3 |  | 0 - 5E+5 | air | 30 | 250 | < 1 |  | 0% (autozero) | 0.05 |  | 3-6 months | up to 64 ports | Ion Mobility Spectrometry (IMS) | 2013
| DMSO (Dimethyl-sulfoxide) as individual compound | 67-68-5 | 100 | 0 - 1E+6 | air & nitrogen | 180 | 50-500 | 5 | 10 | 0% (weekly zero) |  |  | 3-6 months | up to 64 ports | Proton Transfer TOF-MS (PTR-MS) | 2021 | ●
| Edition 2022, Table YE4a | Table YE4a has been updated based on the technical information available and evaluated by IRDS experts in the year of evaluation 2021
| * Range that can be calibrated and renders reliable results | [13 empty] | Methods and instruments are known and are being optimized
| ** Indicate also typical sampled volume to render a datapoint/reading | [13 empty] | Methods and instruments are known and in preparation for production
| *** Indicate typical time period for drift consideration and zero point re-calibration | [13 empty] | Methods and instruments are in beta tool status under qualification
**** Indicate typical time period for span drift consideration and re-calibration
***** Monitor can be used in an automated multi-sampling point environment
****** "Total" analyzers may have different response factors to individual contaminants, and therefore may over or under report actual gas-phase concentrations.

## Notes for Table YE4a
INDEX
Notes for Table YE4a
* Range that can be calibrated and renders reliable results
** Indicate also typical sampled volume to render a datapoint/reading
*** Indicate typical time period for drift consideration and zero point re-calibration
**** Indicate typical time period for span drift consideration and re-calibration
***** Monitor can be used in an automated multi-sampling point environment; how many ports/time resolution?
****** "Total" analyzers may have different response factors to individual contaminants, and therefore may over or under report actual gas-phase concentrations.

## Table YE5
INDEX | NEW: Table YE5 Yield requirements for MEMS production
NEW: Table YE5 Yield requirements for MEMS production
| Year of Production | 2018 | Mid term (3-5 years)
Infrared inspection with automated and fullwafer scan
| Defect types for surface MEMS technology(A) | particles, foreign materials, cracks | particles, foreign materials, cracks
| Defect types for bulk technology(A) | wafer bond quality, buried particles, cracks | wafer bond quality, buried particles, cracks
| wafer thickness for surface MEMS technology(A) | 250 um - 1,5 mm | 250 um - 2 mm
| wafer thickness for bulk technology(A) | 300 um - 4 mm | 300 um - 4 mm
| Thruput at Resolution 4 um (200 mm wa/hrs) (C) | 10 | 25
| Thruput as Resolution 1 um (200mm wa/hrs) (C) | 3 | 5
| Illumination mode (B) | reflexion and transmission plus infrared dark field mode | reflexion and transmission plus infrared dark field mode
| Wafer size (mm) | 200 | 300
| Wafer bow plus/minus for handling and automatic focus adjustment (um) | 400 | 600
| Repeatability (% of defects in 10 runs) | 95 | 95
| KLARF | yes | yes
MEMS specific additional requirements to a review tool for wafer with backside structure
| wafer thickness for surface MEMS technology(A) | 250 um - 2 mm | 250 um - 2 mm
| wafer thickness for bulk technology(A) | 300um-4mm | 300um-4mm
| Wafer backside handling with wafer edge grip (mm) | 5 | 3
| Wafer bow plus/minus for handling and automatic focus adjustment (um) | 400 | 600
| Thruput (at 50 defects per wafer) | 100 wa/hrs | 100 wa/hrs
| Additional illumination mode for bulk technology | infrared | infrared
| Wafer size (mm) | 200 | 300
CD Sem under angle of 45°
| Tilt | 0-60° | 0-60°
| Min, Structure | 1 um | 300 nm
| Max Structure, larger structures can be measured with optical methods | 10 um | 10 um
| Aspect ratio | 10-30 um depth | 50 um depth
| resolution | 1nm | 1nm
| Thruput (20 points/wafer) | 15 wa/hrs | 25 wa/hrs
| Precision | 100 | 100
| Repeatability | 98 | 98
| Wafer size (mm) | 200 | 300
| wafer thickness | 250 um - 1,5 mm | 250 um - 1,5 mm
| wafer bow | 400 | 600
Manufacturable solutions exist, and are being optimized
Manufacturable solutions are known
Interim solutions are known
Manufacturable solutions are NOT known

## Notes for Table YE5
INDEX
Notes for Tables YE5:
(A) definition of technology: till 30 µm depth = surface technology, stacked technologies and those with depth more than 30 µm = bulk technology
(B) infrared dark field mode available but throughput not yet proven
(C) throughput measured using STD wafer, covering MEMS relevant defect types

## Table YE6 Bulk Gases
INDEX | Table YE-6 Bulk Gases Supporting Table for On-line Methods
|  |  | measurement | Measurement Range | Matrix | Notes | Data interval | Sample flow** | response time t95 | recovery time t05 | zero point*** | span drift**** | interference | service interval | multipoint | literature reference
|  | CAS-N° | principle | (pptv)* | (air, others) |  | (sec) | (ml/min) | rise (sec) | decline (sec) | drift (%/month) | (%/month) | to (% of signal) | (months) | sampling capability***** | ( publication with IDM/academia)
| O2 |  | APIMS | 10 pptv | N2
| O2 |  | Coulometric | 45 pptv | N2 |  | 1 | 500 | 30 (t90) | 300 (ppm to ppb) | 0 | 0 | none | customer dependent (usually months) | yes | DF-760E Manual, Theory of Operation Section
| O2 |  | CRDS | 200 pptv | N2 | Requires H2 |  | 500-1800 | 180
| H2 |  | APIMS | 10…150 pptv | N2 |  | 120
| H2 |  | GC | 500 pptv | N2
| H2 |  | CRDS | 8000 pptv | N2 |  |  | 500 | 180
| H2O |  | APIMS | 10 pptv | N2 |  | 120
| H2O |  | CRDS | 100 pptv | N2 |  |  | 2000 | 120
| H2O |  | TDLAS | 55 pptv | N2 |  | 1 | 1000 | 180 (t90, conservative) | 300 (ppm to ppb) | 0 | 0 | NH3 (requires DF740) | as needed (usually years) | yes | DF-760E Manual, Theory of Operation Section
| H2O |  | IMS | 200 pptv | N2
| CO |  | APIMS | 10…50 pptv | N2 |  | 120
| CO |  | GC | 100 pptv | N2
| CO |  | CRDS | 200 pptv | N2 |  |  | 1000 | 60
| CO2 |  | APIMS | 5 pptv | N2 |  | 120
| CO2 |  | GC | 100 pptv | N2
| CO2 |  | CRDS | 100 pptv | N2 |  |  | 1000 sample + 4000 purge | 60
| CH4 |  | APIMS | 10 pptv | N2 |  | 120
| CH4 |  | GC | 500 pptv | N2
| CH4 |  | CRDS | 500 pptv | N2 |  |  | 2000 | 60
| ≤C4 |  | APIMS | 10 pptv | N2 |  | 120
| ≤C4 |  | GC | 100 pptv | N2
| ≤C4 |  | CRDS | 500 pptv | N2 |  |  | ? | ?
| ≥C5 |  | APIMS | 10 pptv | N2 |  | 120
| ≥C5 |  | GC | 100 pptv | N2
| Ar |  | APIMS | 300 pptv | N2 |  | 120
| Ar |  | GC | 500 pptv | N2
| O2 |  | APIMS | 10pptv | Ar |  | 120
| O2 |  | Coulometric | 45 pptv | Ar |  | 1 | 500 | 30 (t90) | 300 (ppm to ppb) | 0 | 0 | none | customer dependent (usually months) | yes | DF-760E Manual, Theory of Operation Section
| O2 |  | CRDS | 90 pptv | Ar | Requires H2 |  | 500-1800 | 180
| H2 |  | APIMS | 10…100 pptv | Ar |  | 120
| H2 |  | GC | 500 pptv | Ar
| H2 |  | CRDS | 6000 pptv | Ar |  |  | 500 | 180
| H2O |  | APIMS | 10…30pptv | Ar |  | 120
| H2O |  | CRDS | 100 pptv | Ar |  |  | 2000 | 120
| H2O |  | TDLAS | 55 pptv | Ar |  | 1 | 1000 | 180 (t90, conservative) | 300 (ppm to ppb) | 0 | 0 | NH3 (requires DF740) | as needed (usually years) | yes | DF-760E Manual, Theory of Operation Section
| H2O |  | IMS | 200 pptv | Ar
| CO |  | APIMS | 10pptv | Ar |  | 120
| CO |  | GC | 100 pptv | Ar
| CO |  | CRDS | 150 pptv | Ar |  |  | 1000 | 60
| CO2 |  | APIMS | 5pptv | Ar |  | 120
| CO2 |  | GC | 100 pptv | Ar
| CO2 |  | CRDS | 100 pptv | Ar |  |  | 1000 sample + 4000 purge | 60
| CH4 |  | APIMS | 10pptv | Ar |  | 120
| CH4 |  | GC | 450 pptv | Ar
| CH4 |  | CRDS | 450 pptv | Ar |  |  | 2000 | 60
| ≤C4 |  | APIMS | 10pptv | Ar |  | 120
| ≤C4 |  | CRDS | 450 pptv | Ar
| ≤C4 |  | GC | 100 pptv | Ar
| ≥C5 |  | APIMS | 10pptv | Ar |  | 120
| ≥C5 |  | GC | 100 pptv | Ar
| N2 |  | APIMS | 300 pptv | Ar |  | 120
| N2 |  | GC | 100 pptv | Ar
| O2 |  | APIMS | 10…30 pptv | H2 |  | 120
| O2 |  | Coulometric | 45 pptv | H2 |  | 1 | 500 | 30 (t90) | 300 (ppm to ppb) | 0 | 0 | none | customer dependent (usually months) | yes | DF-760E Manual, Theory of Operation Section
| O2 |  | CRDS | 150 pptv | H2 | Requires H2 |  | 500-1800 | 180
| H2O |  | APIMS | 10…30 pptv | H2 |  | 120
| H2O |  | CRDS | 100 pptv | H2 |  |  | 2000 | 120
| H2O |  | TDLAS | 55 pptv | H2 |  | 1 | 1000 | 180 (t90, conservative) | 300 (ppm to ppb) | 0 | 0 | NH3 (requires DF740) | as needed (usually years) | yes | DF-760E Manual, Theory of Operation Section
| H2O |  | IMS | 200 pptv | H2
| CO |  | APIMS | 10…30 pptv | H2 |  | 120
| CO |  | GC | 100 pptv | H2
| CO2 |  | APIMS | 5…10 pptv | H2 |  | 120
| CO2 |  | GC | 100 pptv | H2
| CO2 |  | CRDS | 500 pptv | H2
| CH4 |  | APIMS | 10 pptv | H2 |  | 120
| CH4 |  | GC | 500 pptv | H2
| CH4 |  | CRDS | 500 pptv | H2 |  |  | 2000 | 60
| ≤C4 |  | APIMS | 10pptv | H2 |  | 120
| ≤C4 |  | CRDS | 500 pptv | H2
| ≤C4 |  | GC | 100 pptv | H2
| ≥C5 |  | APIMS | 10pptv | H2 |  | 120
| ≥C5 |  | GC | 100 pptv | H2
| N2 |  | APIMS | 30 pptv | H2 |  | 120
| N2 |  | GC | 100 pptv | H2
| Ar |  | APIMS | 300 pptv | H2 |  | 120
| Ar |  | GC | 500 pptv | H2
| O2 |  | APIMS | 10pptv | He |  | 120
| O2 |  | Coulometric | 45 pptv | He |  | 1 | 500 | 30 (t90) | 300 (ppm to ppb) | 0 | 0 | none | customer dependent (usually months) | yes | DF-760E Manual, Theory of Operation Section
| O2 |  | CRDS | 50 pptv | He | Requires H2 | 500-1800 | 180
| H2 |  | APIMS | 10…50pptv | He |  | 120
| H2 |  | GC | 500 pptv | He
| H2 |  | CRDS | 4000 pptv | He |  |  | 500 | 180
| H2O |  | APIMS | 10…30pptv | He |  | 120
| H2O |  | CRDS | 100 pptv | He |  |  | 2000 | 120
| H2O |  | TDLAS | 55 pptv | He |  | 1 | 1000 | 180 (t90, conservative) | 300 (ppm to ppb) | 0 | 0 | NH3 (requires DF740) | as needed (usually years) | yes | DF-760E Manual, Theory of Operation Section
| H2O |  | IMS | 200 pptv | He
| CO |  | APIMS | 10pptv | He |  | 120
| CO |  | GC | 100 pptv | He
| CO |  | CRDS | 180 pptv | He |  |  | 1000 | 60
| CO2 |  | APIMS | 5…10pptv | He |  | 120
| CO2 |  | GC | 100 pptv | He
| CO2 |  | CRDS | 100 pptv | He |  |  | 1000 sample + 4000 purge | 60
| CH4 |  | APIMS | 10pptv | He |  | 120
| CH4 |  | GC | 400 pptv | He
| CH4 |  | CRDS | 400 pptv | He |  |  | 2000 | 60
| ≤C4 |  | APIMS | 10pptv | He |  | 120
| ≤C4 |  | CRDS | 400 pptv | He
| ≤C4 |  | GC | 100 pptv | He
| ≥C5 |  | APIMS | 10pptv | He |  | 120
| ≥C5 |  | GC | 100 pptv | He
| N2 |  | APIMS | 30 pptv | He |  | 120
| N2 |  | GC | 100 pptv | He
| Ar |  | APIMS | 300 pptv | He |  | 120
| Ar |  | GC | 500 pptv | He
| H2 |  | APIMS | 10…300 pptv | O2 |  | 120
| H2 |  | GC | 500 pptv | O2
| H2O |  | APIMS | 10…150 pptv | O2 |  | 120
| H2O |  | CRDS | 100 pptv | O2 |  |  | 2000 | 120
| H2O |  | TDLAS | 55 pptv | O2 |  | 1 | 1000 | 180 (t90, conservative) | 300 (ppm to ppb) | 0 | 0 | NH3 (requires DF740) | as needed (usually years) | yes | DF-760E Manual, Theory of Operation Section
| H2O |  | IMS | 200 pptv | O2
| CO |  | APIMS | 10...300 pptv | O2 |  | 120
| CO |  | GC | 100 pptv | O2
| CO |  | CRDS | 180 pptv | O2 |  |  | 1000 | 60
| CO2 |  | APIMS | 5...300 pptv | O2 |  | 120
| CO2 |  | GC | 100 pptv | O2
| CO2 |  | CRDS | 100 pptv | O2 |  |  | 1000 sample + 4000 purge | 60
| CH4 |  | APIMS | 10...300 pptv | O2 |  | 120
| CH4 |  | GC | 500 pptv | O2
| CH4 |  | CRDS | 500 pptv | O2 |  |  | 2000 | 60
| ≤C4 |  | APIMS | 10…300 pptv | O2 |  | 120
| ≤C4 |  | CRDS | 500 pptv | O2
| ≤C4 |  | GC | 100 pptv | O2
| ≥C5 |  | APIMS | 10…300 pptv | O2 |  | 120
| ≥C5 |  | GC | 100 pptv | O2
| N2 |  | APIMS | 30…300 pptv | O2 |  | 120
| N2 |  | GC | 300 pptv | O2
| Ar |  | APIMS | 300 pptv | O2 |  | 120
| Ar |  | GC | 500 pptv | O2
| O2 |  | APIMS | 10pptv | CO2 |  | 120
| O2 |  | CRDS | 300…5000 pptv | CO2 | Requires H2
| H2 |  | APIMS | 10pptv | CO2 |  | 120
| H2 |  | GC | 1000 pptv | CO2
| H2O |  | APIMS | 10pptv | CO2 |  | 120
| H2O |  | TDLAS | ~400 pptv | CO2 |  | 1 | 1000 | 180 (t90, conservative) | 300 (ppm to ppb) | 0 | 0 | NH3 (requires DF740) | as needed (usually years) | yes | DF-760E Manual, Theory of Operation Section
| H2O |  | CRDS | 100...800 pptv | CO2 |  |  | 2000 | 120
| H2O |  | IMS | 500 pptv | CO2
| CO |  | APIMS | 10pptv | CO2 |  | 120
| CO |  | GC | 1000 pptv | CO2
| CH4 |  | APIMS | 10pptv | CO2 |  | 120
| CH4 |  | GC | 1000 pptv | CO2
| ≤C4 |  | APIMS | 10pptv | CO2 |  | 120
| ≤C4 |  | GC | 1000 pptv | CO2
| ≥C5 |  | APIMS | 10pptv | CO2 |  | 120
| ≥C5 |  | GC | 1000 pptv | CO2
| N2 |  | APIMS | 10pptv | CO2 |  | 120
| N2 |  | GC | 1000 pptv | CO2
| Ar |  | APIMS | 10pptv | CO2 |  | 120
| Ar |  | GC | 1000 pptv | CO2
| H20 |  | TDLAS | 55-20000000 | Critical clean dry air |  | 1 | 1000 | 180 (t90, conservative) | 300 (ppm to ppb) | 0 | 0 | NH3 (requires DF740) | as needed (usually years) | yes | DF-760E Manual, Theory of Operation Section
| H2 |  |  |  | Critical clean dry air
| CO |  |  |  | Critical clean dry air
| CO2 |  |  |  | Critical clean dry air
| total base as NH3) |  |  |  | Critical clean dry air
| NH3 (as NH3)) |  | PTR-TOF | 500 - 1,0000,000 | Critical clean dry air |  | 1s-180s | 50-500 | 10 | 20 | 0% (weekly backround) | <10% |  | 3-6 month | yes | [Jordan2009], [Hayeck2014], [Herbig2019]
| total acid including SO2 (as SO4)) |  |  |  | Critical clean dry air
| SO4 (as SO4)) |  |  |  | Critical clean dry air
| Each refractory compound (0rganics containing S, P, Si) |  | PTR-TOF | 50 - 1,0000,000 | Critical clean dry air |  | 1s-180s | 50-500 | 5 | 10 | 0% (weekly backround) | <10% | 0 | 3-6 month | yes | [Jordan2009], [Hayeck2014], [Herbig2019]
| H2O |  | TDLAS | 55-20000000 | N2 |  | 1 | 1000 | 180 (t90, conservative) | 300 (ppm to ppb) | 0 | 0 | NH3 (requires DF740) | as needed (usually years) | yes | DF-760E Manual, Theory of Operation Section
| O2 |  | Coulometric | 45-20000000 | N2 |  | 1 | 500 | 30 (t90) | 300 (ppm to ppb) | 0 | 0 | none | customer dependent (usually months) | yes | DF-760E Manual, Theory of Operation Section
| CO2 |  |  |  | N2
| CO |  |  |  | N2
| H2 |  |  |  | N2
| organics (molecular weight > benzene) normalized to hexadecane equivalent) |  | PTR-TOF | 50 - 1,0000,000 | N2 |  | 1s-180s | 50-500 | 5 | 10 | 0% (weekly backround) | <10% | 0 | 3-6 month | yes | [Jordan2009], [Hayeck2014], [Herbig2019]
| total base (as NH3)) |  |  |  | N2
| total acid (as SO4) including SO2) |  |  |  | N2
| refractory compounds (organics containing S, P, Si, etc.) normalized to hexadecane equivalent) |  | PTR-TOF | 50 - 1,0000,000 | N2 |  | 1s-180s | 50-500 | 5 | 10 | 0% (weekly backround) | <10% | 0 | 3-6 month | yes | [Jordan2009], [Hayeck2014], [Herbig2019]
| H2O |  | TDLAS | 50-20000000 | He |  | 1 | 1000 | 180 (t90, conservative) | 300 (ppm to ppb) | 0 | 0 | NH3 (requires DF740) | as needed (usually years) | yes | DF-760E Manual, Theory of Operation Section
| O2 |  | Coulometric | 45-20000000 | He |  | 1 | 500 | 30 (t90) | 300 (ppm to ppb) | 0 | 0 | none | customer dependent (usually months) | yes | DF-760E Manual, Theory of Operation Section
CO2
| CO |  |  |  | He
H2
| organics (molecular weight > benzene) normalized to hexadecane equivalent) |  | PTR-TOF | 500 - 10,0000,000 | He |  | 1s-180s | 1950-05-01 | 5 | 10 | 0% (weekly backround) | <10% | 0 | 3-6 month | yes | [Jordan2009], [Hayeck2014], [Herbig2019]
| total base (as NH3)) |  |  |  | He
| total acid including SO2 (as SO4)) |  |  |  | He
| refractory compounds (organics containing S, P, Si, etc.) normalized to hexadecane equivalent) |  | PTR-TOF | 500 - 10,0000,000 | He |  | 1s-180s | 1950-05-01 | 5 | 10 | 0% (weekly backround) | <10% | 0 | 3-6 month | yes | [Jordan2009], [Hayeck2014], [Herbig2019]
| H2O |  | TDLAS | 400-20000000 | CO2 |  | 1 | 1000 | 180 (t90, conservative) | 300 (ppm to ppb) | 0 | 0 | NH3 (requires DF740) | as needed (usually years) | yes | DF-760E Manual, Theory of Operation Section
| O2 |  | Coulometric | 45-20000000 | CO2 |  | 1 | 500 | 30 (t90) | 300 (ppm to ppb) | 0 | 0 | none | customer dependent (usually months) | yes | DF-760E Manual, Theory of Operation Section
| CO |  |  |  | CO2
| H2 |  |  |  | CO2
| organics(molecular weight > benzene) normalized to hexadecane equivalent) |  | PTR-TOF | 100 - 1,0000,000 | CO2 |  | 1s-180s | 50-500 | 5 | 10 | 0% (weekly backround) | <10% | 0 | 3-6 month | yes | [Jordan2009], [Hayeck2014], [Herbig2019]
| total base (as NH3)) |  |  |  | CO2
| total acid including SO2 (as SO4)) |  |  |  | CO2
| refractory compounds (organics containing S, P, Si, etc.) normalized to hexadecane equivalent) |  | PTR-TOF | 100 - 1,0000,000 | CO2 |  | 1s-180s | 50-500 | 5 | 10 | 0% (weekly backround) | <10% | 0 | 3-6 month | yes | [Jordan2009], [Hayeck2014], [Herbig2019]
| O2 |  |  |  | Etchants (Corrosive) | BCl3, Cl2, HBr
| H20 |  |  |  | Etchants (Corrosive) | BCl3, Cl2, HBr
| Critical specified metals/total metals ppbw |  |  |  | Etchants (Corrosive) | BCl3, Cl2, HBr
| O2 |  |  |  | Etchants (Non-corrosive)) | C5F8, C4F8, C4F6, CH2F2, SF6
| H2O |  | TDLAS | 5000-100000000 | Etchants (Non-corrosive)) | C5F8, C4F8, C4F6, CH2F2, SF6 | 1 | 1000 | 180 (t90, conservative) | 300 (ppm to ppb) | 0 | 0 | None | as needed (usually years) | yes | DF-760E Manual, Theory of Operation Section
| O2 |  | Coulometeric | 45-20000000 | Etchants | Xe | 1 | 500 | 30 (t90) | 300 (ppm to ppb) | 0 | 0 | none | customer dependent (usually months) | yes | DF-760E Manual, Theory of Operation Section
| H2O |  | TDLAS | 5000-100000000 | Etchants | Xe | 1 | 1000 | 180 (t90, conservative) | 300 (ppm to ppb) | 0 | 0 | None | as needed (usually years) | yes | DF-760E Manual, Theory of Operation Section
| O2 ppm |  |  |  | High k Gate Dielectrics - TMA
| Metals each element ppb |  |  |  | High k Gate Dielectrics - TMA
| Silicon ppm |  |  |  | High k Gate Dielectrics - TMA
| Hydrocarbons ppm |  |  |  | High k Gate Dielectrics - TMA
| Zr -ppm |  |  |  | High k Capacitor Dielectrics - HfCl4
| Metals each element -ppb |  |  |  | High k Capacitor Dielectrics - HfCl4
| Hydrocarbons -ppm |  |  |  | High k Capacitor Dielectrics - HfCl4
| Zr -ppm |  |  |  | High k Capacitor Dielectrics - TDEAH
| Metals each element -ppb |  |  |  | High k Capacitor Dielectrics - TDEAH
| Hydrocarbons -% by NMR |  |  |  | High k Capacitor Dielectrics - TDEAH
| Chloride ppm |  |  |  | High k Capacitor Dielectrics - TDEAH
| Hydroloysis product alkylamine -ppm |  |  |  | High k Capacitor Dielectrics - TDEAH
| Hf ppm |  |  |  | High k Capacitor Dielectrics - TEMAZ -
| Metals each element ppb |  |  |  | High k Capacitor Dielectrics - TEMAZ
| Hydrocarbons % by NMR |  |  |  | High k Capacitor Dielectrics - TEMAZ
| Chloride ppm |  |  |  | High k Capacitor Dielectrics - TEMAZ
| Hydroloysis product alkylamine ppm |  |  |  | High k Capacitor Dielectrics - TEMAZ
| Metals except B, Au, Ag ppb, each |  |  |  | SiCO - Alkylsilanes
| B, Au, Ag ppb, each |  |  |  | SiCO - Alkylsilanes
| H2O ppm |  |  |  | SiCO - Alkylsilanes
| CO, CO2 ppm |  |  |  | SiCO - Alkylsilanes
| Non-methane hydrocarbons C2-C4 ppm |  |  |  | SiCO - Alkylsilanes
| Nitrogen ppm |  |  |  | SiCO - Alkylsilanes
| Ar+O2 ppm |  |  |  | SiCO - Alkylsilanes
| Chloride ppm |  |  |  | SiCO - Alkylsilanes
| Organic Porogen % |  |  |  | Ultra low k Porous OSG / SiCO - DEMS
| metals ppbv total |  |  |  | Titanium nitride - TiCl4 - Purity based upon
| Metals Purity ppbv total |  |  |  | MIM capacitor Electrodes - TiCl4
| Critical specified metals/total metals ppbw |  |  |  | Tantalum Amides
| O2 ppbv |  |  |  | Tantalum Amides
| H2O ppbv |  |  |  | Tantalum Amides
| Hydrocarbons ppm |  |  |  | Tantalum Amides
| O2 ppbv |  |  |  | Titanium Nitride Precursors
| H2O ppbv |  |  |  | Titanium Nitride Precursors
| Hydrocarbons ppm |  |  |  | Titanium Nitride Precursors
| Purity based on metals analyzed ppmv |  |  |  | TDMAT
| Purity based upon metals ppbv total |  |  |  | TiCl4
| Nb ppm |  |  |  | Tantalum Nitride Precursors -
| Metals each element ppb |  |  |  | Tantalum Nitride Precursors -
| Hydrocarbons ppm |  |  |  | Tantalum Nitride Precursors -
| Chloride ppm |  |  |  | Tantalum Nitride Precursors -
| Hydroloysis product alkylamine |  |  |  | Tantalum Nitride Precursors -
| Critical specified metals/total metals ppbw |  |  |  | Tungsten Hexafluoride
| O2 ppbv |  |  |  | Tungsten Hexafluoride
| O2 ppb |  |  |  | High Temperature Si Epitaxy - SiHCl3
| H2O ppb |  |  |  | High Temperature Si Epitaxy - SiHCl3
| Hydrocarbons ppb |  |  |  | High Temperature Si Epitaxy - SiHCl3
| Dopants B, Al, P, As ppb |  |  |  | High Temperature Si Epitaxy - SiHCl3
| Metals like Fe ppb |  |  |  | High Temperature Si Epitaxy - SiHCl3
| Carbon ppb |  |  |  | High Temperature Si Epitaxy - SiHCl3
| Carbon Dioxide ppmv |  |  |  | Epitaxial Si and Ge - GeH4
| Carbon Monoxide ppmv |  |  |  | Epitaxial Si and Ge - GeH4
| Digermane ppmv |  |  |  | Epitaxial Si and Ge - GeH4
| Digermane ppmv |  |  |  | Epitaxial Si and Ge - GeH4
| Nitrogen ppmv |  |  |  | Epitaxial Si and Ge - GeH4
| Methane ppmv |  |  |  | Epitaxial Si and Ge - GeH4
| Oxygen + Argon ppmv |  |  |  | Epitaxial Si and Ge - GeH4
| Trigermane ppmv |  |  |  | Epitaxial Si and Ge - GeH4
| Water ppmv |  |  |  | Epitaxial Si and Ge - GeH4
| Chlorogermanes ppmv |  |  |  | Epitaxial Si and Ge - GeH4
| Germoxanes ppmv |  |  |  | Epitaxial Si and Ge - GeH4
| Hydrogenppmv |  |  |  | Ga(CH3)3 (TMG)
| Iron ppbw |  |  |  | GaN - NH3
| Metals each element total ppb |  |  |  | GaN - NH3
| Total metals ppbw |  |  |  | SiC - C3H8 (propane) -
| O2 ppb |  |  |  | Low Temperature Si/Ge Epitaxy
| H2O ppb |  |  |  | Low Temperature Si/Ge Epitaxy
| Hydrocarbons ppb |  |  |  | Low Temperature Si/Ge Epitaxy
| O2 ppb |  |  |  | POUF - SiH4, Si2H6, GeH4
| H2O ppb |  |  |  | POUF - SiH4, Si2H6, GeH4
| Hydrocarbons ppb |  |  |  | POUF - SiH4, Si2H6, GeH4
| O2 ppbv |  |  |  | POUF - GeH4
| H2O ppbv |  |  |  | POUF - GeH4
| Other dopants ppbv |  |  |  | POUF - GeH4
| O2 ppbv |  |  |  | Deposition Gases CVD/PECVD/ ALD (General)
| H2O ppbv |  |  |  | Deposition Gases CVD/PECVD/ ALD (General)
| Critical specified metals/total metals ppbw |  |  |  | Deposition Gases CVD/PECVD/ ALD (General)
| Dopants ppbv |  |  |  | Deposition Gases CVD/PECVD/ ALD (General)
| Total metals ppbw |  |  |  | Amorphous Carbon (Double Patterning)
| O2 ppb |  |  |  | Deposition gases | (e.g. NH3)
| H2O ppb |  | TDLAS | 1000-20000000 | Deposition gases | (e.g. NH3) | 1 | 1000 | 180 (t90, conservative) | 300 (ppm to ppb) | 0 | 0 | None | as needed (usually years) | yes | DF-760E Manual, Theory of Operation Section
| Critical specified metals/total metals ppbw |  |  |  | Deposition gases | (e.g. NH3)
| O2 ppb |  | Coulometeric | 45-20000000 | Deposition gases | (e.g., N2O, NO) | 1 | 500 | 30 (t90) | 300 (ppm to ppb) | 0 | 0 | none | customer dependent (usually months) | yes | DF-760E Manual, Theory of Operation Section
| H2O ppb |  | TDLAS | 5000-100000000 | Deposition gases | (e.g., N2O, NO) | 1 | 1000 | 180 (t90, conservative) | 300 (ppm to ppb) | 0 | 0 | None | as needed (usually years) | yes | DF-760E Manual, Theory of Operation Section
| Critical specified metals/total metals ppbw |  |  |  | Deposition gases | (e.g., N2O, NO)
| electrical dopants e.g. AsH3, PH3, B2H6 |  |  |  | Deposition gases -
| O2 ppbv |  |  |  | electrical dopants
| H2O ppbv |  |  |  | electrical dopants
| Other dopants ppbv | Other dopants (ppbv) | Other dopants (ppbv) | Other dopants (ppbv) | electrical dopants
| O2 ppbv |  |  |  | Implant gases | AsH3, PH3, BF3
| H2O ppbv |  |  |  | Implant gases (O2, H2O (ppbv))
| Other dopants ppbv |  |  |  | Implant gases (Other dopants (ppbv))
| Other constituents ppbv |  |  |  | Implant gases
| O2 ppbv |  |  |  | Laser gases - Litho
| H2O ppbv |  |  |  | Laser gases - Litho